Committee on Consumer Affairs and Business Licensing

Balqees Mihirig, Senior Counsel

Leah Skrzypiec, Policy Analyst	 Andrew Wilber, Finance Analyst

Committee on Resiliency and Waterfronts

Jessica Steinberg Albin, Counsel

Patrick Mulvihill, Senior Policy Analyst

Jonathan Seltzer, Senior Finance Analyst

Committee on Environmental Protection

Samara Swanston, Counsel

Nadia Johnson, Senior Policy Analyst

Ricky Chawla, Policy Analyst

Jonathan Seltzer, Senior Finance Analyst

## THE COUNCIL OF THE CITY OF NEW YORK

# BRIEFING PAPER OF THE

# GOVERNMENTAL AFFAIRS AND INFRASTRUCTURE DIVISIONS

Jeffrey Baker, Legislative Director

Rachel Cordero, Deputy Director, Governmental Affairs Division

Terzah Nasser, Deputy Director, Infrastructure Division

# COMMITTEE ON CONSUMER AFFAIRS AND BUSINESS LICENSING

# Hon. Rafael L. Espinal, Chair

# COMMITTEE ON RESILIENCY AND WATERFRONTS

# Hon. Justin L. Brannan., Chair

# COMMITTEE ON ENVIRONMENTAL PROTECTION

# Hon. Costa G. Constantinides, Chair

#### September 4, 2019

Oversight: Consolidated Edison Summer 2019 Service Outages

- INTRODUCTION

On September 4, 2019, the Committees on Consumer Affairs and Business Licensing, Resiliency and Waterfronts, and Environmental Protection, will hold an oversight hearing on the Consolidated Edison (Con Ed) power outages that hit New York City over the summer of 2019. The Committees have invited representatives from Con Ed, the New York State Public Service Commission (PSC), the New York City Office of Emergency Management (OEM), the New York City Department of Environmental Protection (DEP), and other interested parties to offer testimony.

- BACKGROUND

- Summer 2019 Outages

In the summer of 2019, New York City experienced a number of serious power outages. The first major outage hit the Upper West Side of Manhattan on July 13. The blackout hit just before 7pm and affected at least 73,000 customers. The outage affected power from 72nd street to the West 40s and all the way from Fifth Avenue to the Hudson River. Over 200 traffic lights went out, causing pedestrians to jump in and direct traffic. The whole subway system was affected; some lines were completely suspended while trains were halted in station or evacuated, and four stations in Manhattan were totally closed to the public. Performances on Broadway, at Lincoln Center and Madison Square Garden were cancelled, and the New York City Fire Department (FDNY) responded to hundreds of calls regarding stuck elevators and automatic alarms. Power was restored to some within approximately three hours and by midnight, all customers had full service again. After their examination of the outages, which involved reviewing 15 years of data, Con Ed determined that a flawed connection between its sensors and protective relays caused the outage.

Within a day of the Manhattan outages, a number of customers on Staten Island were also hit with blackouts. The first left more than 1,300 residents in West Brighton without power. Two days later, after a fire erupted at a Con Ed substation, parts of Staten Island were again disrupted by outages. About 2,200 customers in parts of the East and South shores lost power at about 5pm on July 16 and remained without electricity for approximately 12 hours. However, additional residents reported spotty service during this time where some rooms in their house had power while others did not. Hours after the power was restored to the East and South Shores, nearly 4,000 customers in the New Dorp neighborhood of Staten Island lost power because of Con Ed equipment failure. Traffic signals were out and power was not restored until later that evening. Parts of that neighborhood had already experienced blackouts that day, which affected about 400 customers, while more than 500 residents of Stapleton were also left without power because of equipment failure.

Days after the Manhattan outage, summer storms caused intense rain and sweltering heat. As more residents relied on their air conditioners, pressure on the grid increased, causing a number of manhole fires across Queens and Brooklyn. The manhole fires “were all caused by the rain or overheating wires below the ground.” This resulted in both a loss of power and the evacuation of some buildings due to high carbon monoxide readings. East Elmhurst in Queens was affected by a transformer catching fire leading to a manhole fire, while outages in the Bronx were caused by a feeder cable issue.

On the weekend of July 20, two-thirds of the country were bracing themselves for a severe heat wave. The Weather Service issued heat advisories for numerous regions, as temperatures were expected to go above 100 degrees Fahrenheit. In New York City, which was also experiencing high humidity, the temperature was expected to feel above 100 degrees. At least six deaths were attributed to the heatwave in other states and, as a precaution, New York City canceled both the OZY Fest in Central Park and the NYC Triathlon.

In the early evening of Sunday, July 21, 2019, temperatures rose to 102 degrees Fahrenheit and parts of New York City began losing power. The largest blackouts were in Flushing and Richmond Hill in Queens, Park Slope, Flatbush and Brighton Beach in Brooklyn, and Lincoln Square in Manhattan. Smaller outages were also recorded in parts of the Bronx and Staten Island. In total, approximately 10,000 customers were affected across the five boroughs.

During that Sunday, electricity supply also reached a record output – 12,048 megawatts of power between 4pm and 5pm, higher than the previous 2016 record of 11,855 megawatts. To cope with the increased demand, attend to repairs and prevent further outages, Con Ed intentionally cut power to certain Brooklyn neighborhoods and reduced the power output in others. On the hottest day of the year, Con Ed cut power to 30,000 customers in Canarsie, Mill Basin and Flatbush, and reduced voltage in Prospect Lefferts Gardens, Prospect Heights, Flatlands, Bergen Beach and Georgetown. More than 6,000 customers across Brooklyn and Queens were still without power on the Tuesday morning, as a storm the previous day did further damage to the Con Ed electricity supply.

In addition to the inconvenience of losing power, businesses in New York City faced hefty losses because they were unable to serve their customers without power. Cancelled Broadway shows cost the industry an estimated $3.5 million. The outage on July 13, a Saturday evening, forced many restaurants to close or significantly reduce service on their busiest day. Manhattan seafood restaurant Gloria reported that their sales were down 50 percent. Other restaurants had to close because they were unable to keep their food at safe temperatures. Restaurants in Brooklyn faced similar pressures when they lost power over the heat wave weekend. The owner of Dagan’s Pizza in Brooklyn, Dan Pando, explained that “[b]etween closing the stores early, to losing the product and the food, all the extra work and we needed to rent a special truck only to try to save some [of the food], it’s looking [like we lost] around twelve to fifteen thousand dollars”. The Park Slope Food Coop experienced both partial and full power failures on July 21 and July 29, which resulted in multiple days of selling exclusively nonperishable foods. The July 21st outage, which was caused by a transformer fire, resulted in a partial power loss, but full power was not restored until two days later.

Although residential and commercial customers are able to submit claims for reimbursement from Con Ed for food spoilage costs, there are limits. For instance, residential customers are limited to claiming up to $515 for their food losses while a commercial customer is limited to $10,200. In both instances the claims must be filed within 30 days of the outage and they generally require an itemized list and receipts to prove the loss. Lastly, both commercial and residential food spoilage reimbursement claims require that the power outage last at least 12 hours within a 24-hour time frame. This runs contrary to the food safety guidelines published by the U.S. Department of Health and Human Services, which was developed in partnership with the Department of Agriculture (USDA), Food and Drug Administration, and the Center for Disease and Control, and states that food requiring refrigeration should be discarded within two to four hours of no refrigeration. According to the USDA, food such as meat, fish and eggs need to be stored at temperatures below 40°F in order to be safe. If the power goes out and these items are in a refrigerator, they should remain at safe temperatures for four hours, provided the door remains closed. If these food items were held above 40°F for more than two hours, they should be discarded. Given that the various blackouts that hit New York City during the summer of 2019 lasted more than two hours but, at times, less than 12 hours, many residential and commercial customers will be unable to file a reimbursement claim for food spoilage.

- Con Ed’s Responses to the Outages

In a statement following the July 13 outages in Manhattan, Con Ed claimed they “conducted extensive testing of equipment and a thorough review” of their relay system. Con Ed determined that the system did not perform as designed and they identified “a flawed connection between some of the sensors and protective relays at the substation.” Con Ed subsequently corrected that issue and “out of an abundance of caution” they isolated similar equipment, and will test it before putting it back in service.

Prior to the heat wave weekend, however, the President of Con Ed, Tim Cawley, told reporters that Con Ed was “ready for what the heat will bring.” In preparation, Con Ed dispatched 4,000 employees to work on above- and below-ground equipment, transmission lines and substations, working 12-hour shifts to monitor any issues. According to Mr. Cawley, Con Ed had learned from previous peak demand events, particularly in 2016, and that they were prepared. During his press conference, Mr. Cawley stated that Con Ed “basically spend[s] a full year preparing for the high demand that summer brings” and, over the past year they invested $1.5 billion in their energy-delivery systems. Despite these investments, and the assurances from the Con Ed president that they would not need to resort to “voltage optimization” – where voltage is preemptively lowered to protect equipment when there is particularly high demand – Con Ed resorted to completely cutting power to 33,000 residents in parts of Brooklyn. According to the New York Times, this was due to cable failures at the substation serving the area. Five of the 19 cables failed, leaving 14 to handle a heavier-than-normal electricity flow, possibly resulting in a system-wide failure affecting the entire area. No explanation for the failure was given, other than the cuts being “necessary to prevent longer outages.”

- NEW YORK CITY’S ELECTRICAL SYSTEM

  - Grid and Infrastructure

### For decades, electrical power was supplied to consumers through utility companies holding monopolies over large geographic areas. In April 1996, the Federal Energy Regulatory Commission (FERC), in an attempt to establish a competitive bidding market for the sale of power, ordered electric energy producers to let other companies buy and sell the generated power.  The ensuing deregulation of the energy industry resulted, in theory, in competition in the generation and pricing of electrical power. Con Ed, for example, formerly the primary electric power generator in New York City, sold nearly all of its generating capacity in the City, and consumers may now select from various electricity suppliers. Regardless of the supplier a customer chooses, however, Con Ed-owned transmission lines continue to distribute electricity within the City, providing service in the five boroughs and Westchester County.

### After a power plant’s main generators produce an electrical charge, current is sent through a transformer to regulate the voltage level, ensuring enough pressure to travel long distances.  High-voltage transmission lines carry the powerful current to local substations that step down the voltage. The electricity is distributed through feeder cables to neighborhood transformers and then through smaller distribution lines to individual locations where voltages will generally range from 110 – 240 volts, levels considered safe for residential and commercial use. Con Ed operates 200 independent networks that regulate the flow of electricity.

### One mark of distinction of the New York City power system is the prominence of underground distribution. While protected from physical elements like lightning strikes and falling trees, underground wiring systems face challenges in terms of moisture, decomposition, and, in particular, overheating. When high temperatures linger for days the “pavement soaks up heat and can warm the power equipment below”.

### Distribution systems are generally found in one of two arrangements: radial load areas (found primarily in Staten Island) and network load areas (in most other parts of New York City, including Northwest Queens). A radial system, distributing power in a linear fashion that effectively keeps customers on a more independent distribution system, carries the benefit of isolation; that is, if one part of the distribution system should fail, other customers in the same area may still receive power directly to their homes/businesses, even where those customers are as close to a blackout area as across a street.

### Network load areas, in contrast to radial load areas, produce a series of customers all relying on the same transformer(s) and distribution system. Outages are more common in a radial system than a network system, however, because the radial system entails “fewer redundancies… to compensate for component failures” such as downed overhead lines. Network load area systems facing a component failure such as one failing feeder cable may compensate by transferring that cable’s load to connected cables on the same network; too much load carried on too few cables, however, will result in structural damage to the system. All of Con Ed's network load areas are designed with a certain degree of redundancy in order to accommodate the failure of two feeder cables within a single network. Should one or two feeder cables fail, load will be transferred to the remaining cables. The failure of a third feeder cable, however, would put significant stress on the system and risk extensive damage.

### Across the New York City and Westchester County delivery system, Con Ed has 62 substations and its distribution system features approximately 96,000 miles of underground cable, 43,000 underground transformers, 34,000 miles of overhead electric wires, and 52,000 overhead transformers. Typically, Con Ed provides about 350 kilowatt hours per month to residential customers in New York City.

  - The Regulation of Electricity and Other Utility Providers in New York

### The Public Service Commission (PSC) regulates the reliability and safety of the distribution of electricity, as well as other utilities, throughout New York State. The Commission is also responsible for guaranteeing that adequate service is provided by New York's utilities to best promote the public interest, preserve the public health, and protect those using and those employed in manufacturing and distributing power. To facilitate these goals, customers can file complaints about utility providers with PSC, provided they have attempted to resolve the issue with the company first. After a customer has lodged a formal complaint with PSC, the Commission will investigate and report the findings to the customer and utility. If either party requests a hearing, PSC will facilitate this, with the burden of proof borne by the utility company. Either party may also appeal a PSC decision. Importantly for customers, utility companies are prohibited from terminating service while the complaint is being investigated.

### If the PSC finds rates, charges or classifications are unjustly discriminatory, preferential, or in violation of the law, the Commission can correct rates, charges and classifications for the service to be furnished.  The PSC may also examine all corporations under its supervision to keep informed of the practices, regulations and property employed in their business.

### When a utility company wishes to increase customer rates, it must file a request at the PSC. A rate case is the formal process used by the Commission to determine the amounts to charge customers for electricity, natural gas, private water and steam services provided by regulated utilities. A rate case is a public process through which the utility and intervenors, such as commercial entities, public interest groups, municipal officials and advocacy groups may submit briefs, evidence and testimony regarding the request for a rate increase. The PSC must render a decision within 11 months after a major rate case is filed.

- PATTERN OF OUTAGES AND INFRASTRUCTURE FAILURES

  - Prior Outages and Official Investigations

### The power outages experienced by New Yorkers in the summer of 2019 were, unfortunately, not a unique experience. Con Ed has a history of failing to meet the City’s demand for electricity, due to a raft of systemic failures. For example, in early 2000, then New York Attorney General Eliot Spitzer published a report examining Con Ed’s service outages in the summer of 1999. In 1999, hundreds of thousands of Con Ed’s customers lost power during a heat wave. The most severely hit neighborhood was Washington Heights where about 200,000 people had no power for 18 hours, after Con Ed cut their service to preserve equipment. The Attorney General’s office determined that Con Ed customers lost power because numerous elements of Con Ed’s electricity supply system failed and that their preparations for the heat wave were inadequate.

### In their analysis of Con Ed’s preparedness for the summer cooling season, the Attorney General’s Office concluded that the measures Con Ed undertook were severely inadequate. For instance, they found that Con Ed had failed to identify and repair or replace portions of their underground system that were highly susceptible to damage during the hot weather. The Attorney General’s report also found that the system testing system utilized by Con Ed, which was meant to identify vulnerable feeder cables, was unable to predict the kinds of outages that ultimately occurred. According to the report, Con Ed conducted a myriad of tests on the feeders in Washington Heights, and all passed. Despite these results, seven of the thirteen feed cables failed in that neighborhood. At the time, the inherent flaw in the testing method was that it provided either a pass or fail reading, but did nothing to show how vulnerable the cables were to failure, and therefore provided a false sense of security. The Attorney General recommended Con Ed update its testing system to provide more nuanced results or, if no such tests exist, Con Ed should publicly state that fact and propose alternative means of identifying potentially defective equipment.

### Since 1999, Con Ed’s New York City customers have experienced other major outages. In 2003, an outage hit the whole City and lasted 29 hours. The 2006 outage, which mainly hit Queens, lasted eight days, and in 2012, after Superstorm Sandy, numerous parts of the City experienced outages for days or weeks. Like the 1999 and 2019 outages, all of the blackouts in between were deemed to have been caused by various types of equipment failures.

### In early 2007, the New York State Department of Public Service (DPS) produced a report examining the causes and Con Ed’s response to the 2006 Queens blackout. The events leading up to the 2006 outages parallel the situation leading up the 2019 outages. In 2006, extremely high temperatures were predicted to hit the City and demand for electricity was expected grow. In preparation, Con Ed increased its workforce, as it did in 2019, and prepared itself for quickly addressing any technical difficulties. Despite their efforts, however, Con Ed equipment failed spectacularly, and it left approximately 174,000 people without power or with reduced voltage for more than a week.

### According to Con Ed, the failures in Queens were due to three unrelated events: a fire in an underground conduit; malfunctions in a substation breaker; and an excessive current surge caused when equipment was suddenly turned on. However, DPS attributed the outages to  “the Company’s failure to confront and resolve a multitude of issues associated with its operation, maintenance, and oversight of the network and to recognize and take effective action to limit the extent of the cascading system damage and the resulting consumer impacts.” According to the DPS report, Con Ed’s monitoring system was “woefully inadequate” and that the corrosion of Con Ed’s underground transformers in the network were “alarming.”

  - Continued Failures to Maintain, Upgrade and Modernize Infrastructure

Documents submitted to the PSC during the current 2019 rate case further illustrate Con Ed’s failures to upgrade system infrastructure, despite the company justifying rate increases with costs for such upgrades. The Manhattan blackout that occurred on July 13, 2019, was reportedly caused by the failure of both the primary and backup relay systems at the West 65th Street substation. The failure at the 65th street substation led to the failure of a second substation, located at the West 49th Street substation. A filing submitted as part of Con Ed’s Report on 2013 Capital Expenditures noted that 90 percent of Con Ed’s relays at the time were of the electromechanical variety, an obsolete technology, which in their own words, were “prone to mis-operate, causing unnecessary trips,” and for which replacement parts had been out of production for 20 years. However, a list of substation operations capital projects the company submitted in 2009 identified $40 million in funds earmarked for substation relay upgrades. Con Ed’s 2012 rate plan filing requested $26 million for substation relay upgrades, budgeted $3 million, and subsequently spent $0 on these upgrades. The 2016 substation operations and capital budget requested and budgeted $1 million for relay protection communication upgrades, of which $0 were subsequently spent.

Similarly, in 2008, PSC approved a number of energy efficiency programs submitted from utility companies such as Con Ed.  In current rate case, David Bomke, from the New York Energy Consumers Council, testified that Con Ed currently has more than $100 million in unspent funds from these programs that were collected from ratepayers between December 2007 and December 2015.

A Con Ed spokesperson recently reported that Con Ed spent $1.5 billion last year to upgrade its transformers and replace underground feeder cables. However, although this number appears significant, according to experts, such upgrades are routine maintenance projects that utilities need to conduct to ensure that the grid keeps functioning. Furthermore, Con Ed’s prioritization of projects and focus on replacing equipment appears insufficient to respond to the City’s increasing energy demands. In their testimony on the recent rate case, witnesses testifying on behalf of the City expressed concern that Con Ed was not adequately prioritizing its list of projects, and they questioned Con Ed’s decision to stage the projects over time. They highlighted the fact that Con Ed’s focus on replacing equipment was shortsighted, and called for a paradigm shift in the Company’s approach. Rather than focus on mere maintenance and equipment replacement, they testified that the Company must “examine opportunities to invest in research and development, demonstration projects and alternative solutions such as [non wire solutions or NWS] to replacing failed equipment, remediate degraded performance, reduce the cost to maintain, or extend the life of existing assets, and avoid, postpone or reduce capital investment in “like-for-like” asset replacement.”

  - High Customer Rates

### Despite the continued failure of Con Ed to meet the City’s electricity demand, New York City consumers pay some of the highest prices in the Country for their electricity. In their data tracking electricity prices since 2015, the U.S. Bureau of Labor Statistics reports that New Yorkers have consistently paid far above the national average price, illustrated in the chart below:

### Average prices for electricity, the United States and New York-Newark-Jersey City

### The May 2019 prices are 43 percent higher than the national average while the 2018 New York rates were 54 percent higher than the national average.

### Meanwhile, on January 17, 2019, Con Edison declared an increased quarterly dividend of 74 cents a share, the 45th consecutive year of increased dividends, for shareholders. It is the only utility on the S&P 500 Dividend Aristocrats indexthat lists stocks in the S&P 500 index with 25 or more consecutive years of dividend increases. With a current dividend yield of 3.8 percent, it nearly doubles the 2 percent average dividend yield of the S&P 500 Index.

Consumer advocates have repeatedly argued that Con Ed’s rate increases are unjustified and stem from a desire to increase shareholder profitability as opposed to providing adequate services. The witnesses appearing before PSC on behalf of the City testified that Con Ed appeared to consider consumer rates “an unlimited source of funding,” and that they failed “to exercise constraint in determining the scope and magnitude” of its requests for rate increases.”

During the company’s accounting panel testimony submitted as part of the current rate case, a desire for increased return on equity is explicitly mentioned as one of the driving factors behind the proposed rate increases. Karl R. Rábago, Executive Director of the Pace Energy and Climate Center at the Elisabeth Haub School of Law, submitted testimony asserting that the company is attempting to mischaracterize demand related costs as customer costs, in an attempt to inflate the fixed per customer charge billed to individual ratepayers. One example of this is the company’s attempt to characterize the costs of every transformer up to 16 and including 25 kVA in size as a part of its minimum system customer component of transformers despite the fact that they each serve multiple customers as opposed to individual ratepayers. Some have argued that the company is also attempting to build out new and far more extensive natural gas delivery pipelines under the guise of maintenance and repair work, potentially saddling ratepayers with stranded costs related to the construction of infrastructure that goes against state and city emissions reductions targets.

Con Edison has also been criticized for passing the cost membership in trade associations such as the Edison Electric Institute (EEI) and the American Gas Association (AGA) to customers. Notably, both trade associations have funded anti-climate science and anti-renewable energy lobbying efforts undertaken by the American Legislative Exchange Council (ALEC), which provides state legislators with “model policies” to oppose renewable energy standards and overturn laws that reduce carbon dioxide emissions.

- FUTURE PRESSURES ON THE ELECTRICITY GRID

The heatwave that hit the Country in July 2019 was not an isolated event. Across Europe, multiple countries experienced record temperatures and July 2019 is now regarded as the hottest month ever recorded in human history. Temperatures have been rising more rapidly over the last century and currently, one in ten Americans are living in rapidly heating regions, including New York City.  According to a study by the University of Maryland published this year, temperatures in New York City will be up to 5℃ warmer, with a climate similar to Jonesboro, Arkansas by 2080.

Heatwaves in the City are exacerbated by the Urban Heat Island Effect (UHIE), a phenomenon in which urban areas experience higher temperatures than surrounding suburban and rural areas, largely because of heat-retaining concrete and asphalt, less vegetation and more industrial functions. Urban areas can be up to 5.4 degrees warmer during the day and up to 22 degrees hotter at night than surrounding rural and suburban areas, affecting city residents’ quality of life and the City’s infrastructure.  For example, buildings retain heat overnight, which prevents people from sleeping well, air pollution can be worse on hotter days and that may lead to respiratory problems, and warmer conditions may also lead to heavy rainfall causing flooding.  By 2050, the frequency of heat waves and the number of days above 90 degrees is expected to triple.

In conjunction with high temperatures, there is also a high demand for electricity to run air conditioners in buildings and households throughout the City. Excessive electricity use can cause portions of the grid to fail. Extreme heat can also cause infrastructure problems in cities, such as asphalt melting and rail tracks expanding, and can affect efficient functions at airports.

In addition to heat, coastal flooding, exacerbated by climate change, will put pressure on the grid and critical infrastructure.  The New York City Panel on Climate Change (“NPCC”) projects that today’s 100-year flood will become more frequent, occurring on average every 28-71 years by the 2050s.  Some electrical equipment “can suffer catastrophic failures” when they come in contact with water, as evidenced when Superstorm Sandy caused a submerged transformer near a substation near the East River to explode.

After Superstorm Sandy hit in 2012 and left New Yorkers without power for weeks, Governor Cuomo established the Moreland Commission to examine the preparedness of utilities in such weather events. The analysis found that the State had around 270,000 properties that were at risk of damage from storm surges, which could result in a loss of $135 billion. The vulnerabilities highlighted in the report, in addition to concerns raised by various advocates in the 2013 Con Ed rate increase request, resulted in a landmark deal between PSC and Con Ed in 2014. The agreement, the first of its kind in the country, mandated Con Ed to “carry out [an] immediate and comprehensive assessment of climate risks to its power grid…[and] factor the data into all of its long-term planning, construction and budget decisions.”

### As part of the climate change mitigation requirement, Con Ed’s New York ratepayers funded $1 billion in resiliency measures for Con Ed. These funds were acquired to assist Con Ed in meeting its plan to “add a foot to floodwalls around substations and transformers to help prevent storm water from swallowing and frying the equipment…strengthen poles to withstand thrashing winds, move many high-voltage power lines underground and install back-up fuel supply systems to prevent soaring demand during heat waves from crashing the grid” by 2016.

Additionally, in February 2019, Con Ed purchased six new mobile medium-voltage substations used for rapid emergency response from Siemens, a global pioneer in electrical engineering. These substations should give Con Ed the ability to deploy and fully operate a power substation within days instead of months it takes to replace damaged gear.  The mobile substations should increase resilience by reducing the impact of power outages during extreme weather conditions or unexpected events.

The 2014 agreement also required Con Ed  to produce a Climate Change Vulnerability Study (CCVS), which would assess how more frequent and intense weather conditions, including storm surge, wind, rain, snow, ice, temperature variations, humidity and heat waves would affect the City’s electrical grid and Con Ed’s operations in the long-term.  In its 2015 report to the PSC on the status of its storm hardening and resiliency work, Con Ed stated: “An understanding of these key climate and weather factors, as well as those applicable to flooding, is an essential building block in determining the system and equipment design standards and consequent infrastructure investments necessary to improve system resilience to the effects of future climate change.”  The CCVS was due to PSC in 2018, but Con Ed has not publicly released the first chapter.  In a January 2019 report, Con Ed stated that the Study is scheduled to be completed by the end of 2019, and that it “will include a portfolio of operational and design changes designed to manage the risks posed by a changing climate, as well as an assessment of the costs and benefits of those changes.”

In the current PSC rate case, Con Ed provided a draft of CCVS Chapter 2: Humidity, Temperature Variable, & Load in response to the City’s discovery request.  This chapter, however, has not been publicly released.  In the draft chapter, Con Ed identified heat waves as a primary concern for the Network system, which houses the majority of load.  Con Ed projects that because of climate change, system peak loads in 2050 will be 13-24% higher.  Additionally, underground electric power equipment will have higher failure rates during heat waves because heat accumulates underground.  Approximately 87 percent of Con Ed’s distribution capacity is underground (which includes 65 second contingency networks and 19 first contingency networks).  Con Ed determined that by mid-century, between 11 and 28 of its networks may not be able to maintain reliability as they are currently operating.  Adaptation measures that Con Ed proposed for the underground network to address increased demand on load because of climate change include: incorporating distributed energy resources (DERs), complete paper insulated lead cable (PILC) replacement; creating primary feeder loops within or between networks; improving fault monitoring capabilities; and splitting the network into two smaller networks.

However, Con Ed “will not consider immediate adoption and implementation of any of the discrete recommendations that have already been advanced in completed chapters of the [CCVS]” because “immediate implementation . . . would not accommodate the ability to capture synergies or avoid duplicity in our actions.”  Con Ed has stated that the final published CCVS “will include a portfolio of operational, planning and design measures, along with a timeframe to improve our resiliency to climate change.”

Con Ed’s current resiliency plans include many of the same elements that it included in its previous filings with the PSC, including open wire cable replacements, breakaway service connectors, installation of trip saves, and reconfiguring of auto-loop schemes.  As part of its storm hardening efforts from 2013 to 2018, Con Ed hardened or protected its substations, generating facilities and other buildings to the FEMA flood level plus three feet (“+3”).  Con Ed has proclaimed this is sufficiently protective and the “scale of work to build beyond the FEMA +3 level at many of the company affected locations varied from impractical to prohibitive.”  Con Ed chose the FEMA +3 level as its design basis for all new construction, but stated that its major substations, facilities and buildings built after 2005 (Hurricane Katrina) have all exceeded the current FEMA +3 design basis.  However, Con Ed has not addressed why it has not hardened or protected these substations, facilities and buildings to the FEMA flood level plus five feet, which would account for a 500-year storm event, an increasingly more common scenario.  Con Ed only states that it “is further considering this issue as part of its [CCVS].”

- CONCLUSION

In its evaluative report on widespread blackouts in New York City, the Office of the New York Attorney General concluded that “design and maintenance problems endemic to Con Edison’s distribution system led to a total blackout of this network…Con Edison’s customers cannot be put in jeopardy, in the 21st century, of a reoccurrence of the events of July 1999,” and yet, twenty years later, that is still the threat that Con Ed’s customers in New York City are facing. Despite numerous inquiries, commitments, investments and increased rates, Con Ed has failed to address the significant flaws within its delivery system so that it can reliably meet the City’s electricity needs. As the demand for air-conditioning increases, due to rising temperatures, the urban heat island effect and other impacts of climate change, customers will be drawing more from the grid. In addition to the growing demand, the effects of climate change, particularly rising temperatures and storm surges, will put extra pressure on Con Ed’s aging infrastructure, and it is unclear whether the utility has made the required adjustments.

James Barron and Mihir Zaveri “Power restored to Manhattan’s West Side after major blackout”, New York Times, July 13, 2019, available at: https://www.nytimes.com/2019/07/13/nyregion/nyc-power-outage.html.

Id.

Derek M. Norman “The 1977 blackout in New York City happened exactly 42 years ago”, New York Times, July 14, 2019, available at: https://www.nytimes.com/2019/07/14/nyregion/1977-blackout-photos.html?action=click&module=RelatedCoverage&pgtype=Article&region=Footer.

Spencer Kimball “Power restored in Manhattan after blackout left over 70,000 Con Edison customers in the dark”, CNBC, July 13, 2019, available at: https://www.cnbc.com/2019/07/13/massive-outages-leave-27000-coned-customers-without-power-in-new-york-city.html; and James Barron and Mihir Zaveri, at note 1.

Eyewitness News “Power restored to all customers following massive outage in Manhattan”, ABC7NY, July 14, 2019, available at: https://abc7ny.com/major-power-outage-reported-in-manhattan/5393772/.

James Barron and Mihir Zaveri, at note 1.

Con Edison “Con Edison statement: Re: West Side outage root cause”, July 29, 2019, available at: https://www.coned.com/en/about-us/media-center/news/20190729/con-edison-statement.

Joseph Ostapiuk “West Brighton outage leaves over 1,300 without power”, SI Live, July 14, 2019, available at: https://www.silive.com/news/2019/07/west-brighton-outage-leaves-over-1300-without-power.html.

Jen Chung “Power restored to 2,200 Con Ed customers after Staten Island substation fire”, Gothamist, July 17, 2019, available at: https://gothamist.com/2019/07/17/staten_island_power_outage.php.

Id.

Joseph Ostapiuk “Oakwood, New Dorp outage leaves more than 3,000 without power”, SI Live, July 17, 2019, available at: https://www.silive.com/news/2019/07/oakwood-new-dorp-outage-leaves-over-3000-without-power.html.

Jen Chung “Neighborhoods experience power outages across NYC”, Gothamist, July 18, 2019, available at: https://gothamist.com/2019/07/18/power_outages_nyc.php.

Id.

Eyewitness News “Hotel evacuated, power outages after manhole fires in Brooklyn, Queens”, ABC7NY, July 18, 2019, available at: https://abc7ny.com/5403170/?ex_cid=TA_WABC_TW&utm_campaign=trueAnthem:+New+Content+(Feed)&utm_content=5d303c20ca1d050001065b46&utm_medium=trueAnthem&utm_source=twitter.

Jen Chung, at note 12.

Katie Reilly and Josiah Bates “An ‘extremely dangerous’ heat wave will hit 195 million Americans this weekend. Here’s how to stay safe”, Time, July 19, 2019, available at: https://time.com/5628121/united-states-heat-wave-july/.

Id.

Justin Carissimo “Massive heat wave blamed for at least 6 deaths”, CBS News, July 21, 2019, available at: https://www.cbsnews.com/live-news/heat-wave-2019-extreme-heat-advisory-warning-deaths-latest-weather-forecast-us-nyc-2019-07-20/.

Max Jaeger “10,000 New Yorkers lose power at height of Sunday heat”, NY Post, July 21, 2019, available at: https://nypost.com/2019/07/21/10000-new-yorkers-lose-power-at-height-of-sunday-heat/.

Id.

Id.

Id.

Chris Perez “ConEd taking 30K people off power for repairs, says de Blasio”, NY Post, July 21, 2019, available at:  https://nypost.com/2019/07/21/con-ed-taking-30k-people-off-power-for-repairs-says-de-blasio/.

Nicole Brown “Thousands of Con Ed customers in Brooklyn, Queens lose power during heat wave”, AM New York, July 23, 2019, available at: https://www.amny.com/news/con-edison-brooklyn-power-1.34149747.

Cathy Burke “Con Ed figures it out: July 13 blackout cause was little problem that got out of hand in a big way”, New York Daily News, July 29, 2019, available at: https://www.nydailynews.com/new-york/ny-con-ed-blackout-20190729-3gz77uowqvdpnnn6ijdbyzdetq-story.html.

Stefanie Tuder “NYC power outages have had ‘devastating’ effects on restaurants”, Easter New York. July 23, 2019, available at: https://ny.eater.com/2019/7/23/20706978/nyc-blackout-power-outage-pure-thai-gloria-restaurants.

Dan Pando, as quoted by Ellie Plass “Brooklyn businesses and restaurants impacted by blackout”, Bklyner, July 23, 2019, available at: https://bklyner.com/brooklyn-businesses-and-restaurants-impacted-by-blackout/.

John B. Thomas “Coop weather extreme heat, storms, and power outages in July”, Linewaiters’ Gazette, August 15, 2019, available at: https://www.foodcoop.com/wp-content/uploads/2019/08/19-8-15-pgs-1-12.pdf.

Con Ed “Residential claim for food and prescription medicine spoilage”, available at: https://www.coned.com/-/media/files/coned/documents/services-outages/claim-form/residential/residential_claim_form-2017_en.pdf?la=en.

Con Ed “Commercial claim for perishable merchandise”, available at: https://www.coned.com/-/media/files/coned/documents/services-outages/claim-form/commercial/commercial-claim-form-english.pdf?la=en.

U.S. Department of Health and Human Services “Food safety during power outage”, April 12, 2019, available at: https://www.foodsafety.gov/food-safety-charts/food-safety-during-power-outage.

U.S. Department of Agriculture “Keeping food safe during an emergency”, July 30, 2013, available at:  https://www.fsis.usda.gov/wps/portal/fsis/topics/food-safety-education/get-answers/food-safety-fact-sheets/emergency-preparedness/keeping-food-safe-during-an-emergency/CT_Index.

Con Ed “Re: West Side outage root case”, July 29, 2019, available at: https://www.coned.com/en/about-us/media-center/news/20190729/con-edison-statement.

Id.

Id.

Tim Cawley as quoted by: Maura Grunlund “Con Ed is ready for NYC heat wave that ‘will rival’ top weekend demand for electricity”, SI Live, July 19, 2019, available at: https://www.silive.com/news/2019/07/con-ed-is-ready-for-nyc-heat-wave-that-will-rival-top-weekend-demand-for-electricity.html.

Maura Grunlund, id.

Tim Cawley as quoted by id.

Maura Grunlund, id.

Michael Gold and Patrick McGeehan “Con Edison points to record-breaking power usage to explain shutdown”, New York Times, July 22, 2019, available at: https://www.nytimes.com/2019/07/22/nyregion/brooklyn-power-outage-nyc.html.

Con Ed “Re: Southeast Brooklyn outages”, July 22, 2019, available at: https://www.coned.com/en/about-us/media-center/news/20190722/con-edison-statement.

Con Ed “Our business”, available at:  https://www.conedison.com/en/about-us/our-businesses.

Emily S. Rueb “How New York City gets its electricity”, New York Times, February 10, 2017, available at: https://www.nytimes.com/interactive/2017/02/10/nyregion/how-new-york-city-gets-its-electricity-power-grid.html.

David R. Baker and Will Wade “Con Edison prepares for record power demand as NYC bakes in heat”, Bloomberg, July 19, 2019, available at: https://www.bloomberg.com/news/articles/2019-07-19/a-week-after-manhattan-went-dark-con-edison-faces-a-heat-wave.

Office of the New York State Attorney General “Con Edison’s July 1999 Electric Service Outages: A Report to the People of the State of New York” March 9, 2000, available at: https://www.ag.ny.gov/sites/default/files/press-releases/archived/coned.pdf, p. 50.

Id, p. 20.

Con Ed “Company history and statistical information”, available at: https://www.coned.com/en/about-us/corporate-facts.

Id.

NYS Department of Public Service “Meet the Commissioners”, July 23, 2019, available at: http://www3.dps.ny.gov/W/PSCWeb.nsf/All/553FBA3F3EEF7FBD85257687006F3A6D?OpenDocument.

New York’s Utility Project “Filing complaints”, available at: https://utilityproject.org/get-help/filing_complaints/.

NYS Public Service Law § 80

NYS Department of Public Service, “Major Rate Case Process Overview,” available at: https://www3.dps.ny.gov/W/PSCWeb.nsf/All/364D0704BEEC5B7D85257856006C56B3?OpenDocument

Office of the Attorney General, at note 45, p. 1.

Id, p. 7.

Id, pp. 69-70.

Id, pp. 34-35.

Id, pp. 35-40.

Id, p. 72.

Lauren Cook “A brief history of blackouts in New York City”, AM New York, July 15, 2019, available at: https://www.amny.com/news/blackouts-nyc-1.33881190.

Id.

Department of Public Service “Staff report on its investigation of the July 2006 equipment failures and power outages in Con Edison’s Long Island City network in Queens country, New York”, February 2007, available at: http://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B74D61DEC-A052-4433-A4C3-27D863DFF53A%7D, p. 1.

Id, p. 2.

Id, p. 5.

Id, p. 6.

Id, p. 6.

Consolidated Edison Company of New York. Report on 2016 Capital Expenditures and 2017-2021 Electric Capital Forecast, available at: http://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId={1A1D7267-D2A8-4C5C-966C-892A67646B09}.

Patrick McGeehan “A Burning 13,000-Volt Cable Touched Off Manhattan Blackout, Con Edison Says”, The New York Times, July 15, 2019, available at: https://www.nytimes.com/2019/07/15/nyregion/nyc-blackout-con-edison.html.

Id.

Consolidated Edison Company of New York. Exhibit IIP-6, available at: http://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId={1BA71027-19F1-4DB4-8F83-F8629C717721}.

Consolidated Edison Company of New York. Exhibit IIP-9, available at: http://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B4A0055C7-E6A1-4F79-BDFF-C1DC268B0513%7D.

Consolidated Edison. Report on 2012 Capital Expenditures, available at:  http://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId=%7B3CFA4A19-174E-4C2C-989B-EAEBA802AC8D%7D.

Consolidated Edison “Report on 2016 Capital Expenditures and 2017-2021 Electric Capital Forecast”, available at:  http://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId={1A1D7267-D2A8-4C5C-966C-892A67646B09}.

David F. Bomke, Testimony to the NYS Department of Public Service on Consolidated Edison of New York rate case 19-G-0066, filed May 24, 2019, available at: http://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId={8DAF594C-2273-4A06-99B2-868F7C86D949}.

Gwynne Hogan “’They dragged their feet’: Con Ed’s plan for heat waves is years behind schedule”, Gothamist, July 24, 2019, available at: https://gothamist.com/2019/07/24/con_ed_heat_wave_plan_years_late.php.

Susanne DesRoches, Andrew Manshel and Jaime Torres-Springer, on behalf of the City of New York, Testimony to the NYS Department of Public Service on Consolidated Edison of New York rate cases 19-E-0065 and 19-G-0066, filed May 24, 2019, available at: http://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId={E7DE36F2-BDD0-48F9-A97A-5561CD5CAD4C}, p. 32.

Ke Wei, John Marczewski, P.E. and Alex Boutsioulis, P.E. , on behalf of the City of New York, Testimony to the NYS Department of Public Service on Consolidated Edison of New York rate cases 19-E-0065 and 19-G-0066, filed May 24, 2019, available at: http://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId={9D8B94B8-7698-463B-AE0A-5B645CE6461F}.

U.S. Bureau of Labor Statistics “Average energy prices, New York-Newark-Jersey City – May 2019”, available at: https://www.bls.gov/regions/new-york-new-jersey/news-release/averageenergyprices_newyorkarea.htm.

Id.

“Con Edison Declares Common Stock Dividend”, Global News Wire, January 17, 2019, available at: https://www.globenewswire.com/news-release/2019/01/17/1701692/0/en/Con-Edison-Declares-Common-Stock-Dividend.html.

Philip Van Doorn “Dozens of Dividend Aristocrat stock have been big winners in 2019”, July 28, 2019, available at: https://www.marketwatch.com/story/heres-how-all-the-dividend-aristocrat-stocks-have-performed-this-year-2019-07-25.

Ben Reynolds “Con Ed Dividend Built for Recession”, NewsMax, August 22, 2019, available at: https://www.newsmax.com/finance/benreynolds/consolidated-edison-dividend-aristocrat/2019/01/08/id/897378/.

Susanne DesRoches, et al, at note 75, p. 33.

Consolidated Edison Company of New York, Inc. Electric Case Testimonies Volume 1, available at:

http://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId={3CB2AB7C-BE60-4178-A121-5AF4153998B3}.

Direct Testimony of Karl R. Rabago on behalf of Pace Energy and Climate Center, available at: http://documents.dps.ny.gov/public/Common/ViewDoc.aspx?DocRefId={C482767B-7381-4F62-B92C-CBF8374AA424}.

Id.

Id.

Id.

Id.

Brady Dennis and Andrew Freedman “Here’s how the hottest month in recorded history unfolded around the world”, Washington Post, August 5, 2019, available at: https://www.washingtonpost.com/climate-environment/2019/08/05/heres-how-hottest-month-recorded-history-unfolded-around-globe/.

Steven Mufson, Chris Mooney, Juliet Eilperin and John Muyskens, “2℃: Beyond The Limit, Extreme Climate Change has Arrived in America,” The Washington Post, August 13, 2019, available at: https://www.washingtonpost.com/graphics/2019/national/climate-environment/climate-change-america/.

Pam Radtke, “Death, blackouts, melting asphalt: ways the climate crisis will change how we live,” The Guardian, August 20, 2019, available at: https://www.theguardian.com/cities/2019/aug/20/death-blackouts-melting-asphalt-ways-the-climate-crisis-will-change-how-we-live?utm_campaign=citylab-daily-newsletter&utm_medium=email&silverid=%25%25RECIPIENT_ID%25%25&utm_source=newsletter.

Id.

See: “Cool Neighborhoods NYC: A Comprehensive Approach to Keep Communities Safe in Extreme Heat,” June 2017, available at: https://www1.nyc.gov/assets/orr/pdf/Cool_Neighborhoods_NYC_Report_FINAL.pdf

Pam Radtke, at note 91.

Id.

“New York City Panel on Climate Change 2019 Report,” Ch. 4: Coastal Flooding, at 100, available at: https://nyaspubs.onlinelibrary.wiley.com/doi/epdf/10.1111/nyas.14011.

Power grid recovery after natural hazard impact, JRC Science for Policy Report, at 24 (2017), at http://publications.jrc.ec.europa.eu/repository/bitstream/JRC108842/jrc108842kjna28844enn.pdf.

Robert Abrams and Benjamin Lawsky “The Moreland Commission on utility storm preparation and response”, June 22, 2013, available at: https://utilitystormmanagement.moreland.ny.gov/sites/default/files/MACfinalreportjune22.pdf, pp. 35*36.

Maria Gallucci “N.Y. regulator, Con Ed embrace plan to climate-proof power grid”, Inside Climate News, March 12, 2014, available at: https://insideclimatenews.org/news/20140312/ny-regulator-con-ed-embrace-plan-climate-proof-power-grid.

Id.

Id.

See, Siemens Website available at: https://news.usa.siemens.biz/press-release/energy-management/con-edison-strengthens-storm-hardening-efforts-siemens-mobile-substa.

Id.

Id.

Con Ed Report to PSC, “Storm Hardening and Resiliency Collaborative Phase Three Report.” (Sept. 1, 2015), at 117.

Id.

Gwynne Hogan, at note 74.

Con Ed “Electric Long-Range Plan 2019-2038,” (January 2019), at 53.

PSC-Con Ed Rate Case, Exh. NYCEIP-2.

Draft CCVS ch. 2: Humidity, Temperature Variable, & Load, at 4 (Exh. NYCEIP-2).

Draft CCVS ch. 2: Humidity, Temperature Variable, & Load, at 6 (Exh. NYCEIP-2).

Draft CCVS ch. 2: Humidity, Temperature Variable, & Load, at 17 (Exh. NYCEIP-2).  However, most of the company’s distribution capacity for Staten Island is overhead.  Id. at n.9.

Draft CCVS ch. 2: Humidity, Temperature Variable, & Load, at 20 (Exh. NYCEIP-2).

Draft CCVS ch. 2: Humidity, Temperature Variable, & Load, at 42 (Exh. NYCEIP-2).

PSC-Con Ed Rate Case, Exh. NYCEIP-1, at p. 1 of 249.

PSC-Con Ed Rate Case, NYC Electric Infrastructure Panel Testimony, at 32.

PSC-Con Ed Rate Case, Exh. NYCEIP-1, at p. 96-98 of 249.

Id.

Id.

Office of the Attorney General, at note 45.