Preconsidered Proposed Int. No. 1490-A

By Council Member Sanchez (by request of the Mayor)

..Title

A Local Law to amend the administrative code of the city of New York, in relation to conforming the New York city energy conservation code to the New York state energy code with amendments unique to construction in the city, and to repeal section 28-1001.2 of such administrative code relating to such conforming amendments

..Body

Be it enacted by the Council as follows:

Section 1.  Statement of findings and purpose. The New York State Energy Conservation Construction Code (the “New York State Energy Code”) is promulgated by the State Fire Prevention and Building Code Council pursuant to Article 11 of the New York State Energy Law. In accordance with Article 11, the New York City Energy Conservation Code is stricter than the New York State Energy Code. The purpose of this local law is to conform the New York City Energy Conservation Code to recent changes in the New York State Energy Code with local law amendments unique to construction in the city.

§ 2. The definition of “New York state energy code” in section 28-1001.1.1 of the administrative code of the city of New York, as amended by local law number 48 for the year 2020, is amended to read as follows:

NEW YORK STATE ENERGY CODE. The term “New York State Energy Code” means the  New York State Energy Conservation Construction Code, constituting part 1240 of title 19 of the New York codes, rules and regulations (19 NYCRR Part 1240), and the publications incorporated by reference in such part, promulgated on [February 12, 2020] October 1, 2025, by the State Fire Prevention and Building Code Council pursuant to Article 11 of the New York State Energy Law.

§ 3. Section 28-1001.2 of the administrative code of the city of New York is REPEALED and a new Section 28-1001.2 is added to read as follows:

§ 28-1001.2 New York city amendments to the New York state energy code. The following New York city amendments to the New York state energy code are hereby adopted as set forth in Sections 28-1001.2.1 and 28-1001.2.2.

§ 28-1001.2.1  New York city amendments to commercial and residential chapters of the New York state energy code.

Chapter 1 [CE] and Chapter 1 [RE]

Delete Chapter C1 and Chapter R1 in their entirety and replace with a new Chapter 1 to read as follows:

CHAPTER 1

ADMINISTRATION

INTRODUCTORY STATEMENT

The New York City Energy Conservation Code (“NYCECC”) is comprised of the publication entitled the 2025 Energy Conservation Construction Code of New York State (“ECCCNYS”) with amendments as enacted into law by the city. Reflecting these amendments to the ECCCNYS, the NYCECC is divided into provisions relevant to commercial buildings and provisions relevant to residential buildings as follows:

1.	The provisions of the NYCECC for commercial buildings are reflected in the state publications incorporated by reference in 19 NYCRR Sections 1240.3 and 1240.5, as amended by Sections 28-1001.2.1 and 28-1001.2.2 of the Administrative Code. Such state publications include (i) Chapters 1 [CE], 2 [CE], 3 [CE], 4 [CE], 5 [CE] and 6 [CE] of ECCCNYS; (ii) the New York State-specific version of the publication entitled “Standard 90.1, Energy Standard for Buildings Except Low-Rise Residential Buildings,” published by the International Code Council,  as incorporated in the ECCCNYS (“2025 NYS ASHRAE 90.1”); and (iii) reference standards incorporated by reference in subdivision (c) of 19 NYCRR Section 1240.3.

2.	The provisions of the NYCECC for residential buildings are reflected in the state publications incorporated by reference in 19 NYCRR Section 1240.4, as amended by Sections 28-1001.2.1 of the Administrative Code.  Such state publications include (i) Chapters 1 [RE], 2 [RE], 3 [RE], 4 [RE], 5 [RE] 6 [RE] and Appendix RF of the ECCCNYS; and (ii) the referenced standards incorporated by reference in subdivision (b) of 19 NYCRR Section 1240.4.

SECTION ECC 101

SCOPE AND GENERAL REQUIREMENTS

101.1 General. These provisions shall be known and cited as the “New York City Energy Conservation Code,” “NYCECC” or “ECC,” and are referred to herein as “this code.” All section numbers in this code shall be deemed to be preceded by the designation “ECC.” Administration and enforcement of this code shall be in accordance with Title 28 of the Administrative Code.

101.1.1 Titles.

The publication entitled  2025 Energy Conservation Construction Code of New York State shall be known as the “ECCCNYS.”

The New York State-specific version of the publication entitled “Standard 90.1, Energy Standard for Buildings Except Low-Rise Residential Buildings,” published by the International Code Council, as incorporated in the ECCCNYS shall be known as “2025 NYS ASHRAE 90.1.” All references in this code to “2025 NYC ASHRAE 90.1” reflect New York City amendments to 2025 NYS ASHRAE 90.1 as amended by Section 28-1001.2.2 of the Administrative Code..

The ECCCNYS, as contained in Part 1240 of Title 19 of the New York Codes, Rules and Regulations, along with the New York City amendments to such ECCCNYS shall be known collectively as the “New York City Energy Conservation Code” or “NYCECC.”

101.1.2 References. Where reference is made within this code to the Building Code of New York State, Existing Building Code of New York State, Fire Code of New York State, Fuel Gas Code of New York State, Mechanical Code of New York State, Plumbing Code of New York State, Property Maintenance Code of New York State or Residential Code of New York State, the reference shall be deemed to be to the analogous provision of the New York City Construction Codes (Title 28 of the Administrative Code), the 1968 Building Code (Chapter 1 of Title 27 of the Administrative Code), the New York City Fire Code (Title 29 of the Administrative Code) or the New York City Electrical Code (Chapter 11 of Title 28 of the Administrative Code).

101.2 Scope. This code regulates the design and construction of commercial buildings and residential buildings, as defined in Chapter C2 and Chapter R2 of this code, accessory structures, building sites, and associated systems and equipment, as well as the repair, addition, alteration, or change of occupancy thereto for the use and conservation of energy and clean energy features, including the reduction in greenhouse gas emissions, over the life of each such commercial and residential building.

101.2.1 Statutory limitations. In the event of an addition to, or alteration of, an existing building or building system in an existing building that does not include a change of occupancy, nothing in the this code shall be interpreted to require any unaltered portion of such existing building or building system to comply with this code.

101.2.2 Occupancy classifications.  For determination of occupancy classification and use within this code, a comparable occupancy classification shall be made to the New York City Building Code.

101.2.3 Reconciliation with New York State Energy Conservation Construction Code. Whenever any provision of the New York State Energy Conservation Construction Code provides for a more stringent requirement than imposed by this code, the more stringent requirement shall govern.

101.2.4 Other laws. The provisions of this code shall not be deemed to nullify any federal, state or local law, rule or regulation relating to any matter as to which this code does not provide, including but not limited to Articles 320 and 321 of Chapter 3 of Title 28 of the Administrative Code.

101.2.5  Exceptions. This code shall not apply to the alterations of existing buildings set forth in items 1 through 7, provided that the alteration will not increase the energy usage of the building:

1. Storm windows installed over existing fenestration.

2. Glass-only replacements in an existing sash and frame, provided that the U-factor and the solar heat gain coefficient (SHGC) shall be equal to or lower than before the glass replacement.

3.	Surface-applied window film installed on existing single-pane fenestration assemblies reducing solar heat gain, provided that the code does not require the glazing or fenestration to be replaced.

4. Reroofing where neither the sheathing nor the insulation is exposed. Roofs without insulation in the cavity and where the sheathing or insulation is exposed during reroofing shall be insulated either above or below the sheathing.

5. Replacement of existing doors that separate conditioned space from the exterior shall not require the installation of a vestibule or revolving door, provided, however, that an existing vestibule that separates a conditioned space from the exterior shall not be removed.

6. An alteration that replaces less than 10 percent of the luminaires in a space, provided that such alteration does not increase the installed interior lighting power.

7. An alteration that replaces only the bulb and ballast within the existing luminaires in a space, provided that such alteration does not increase the installed interior lighting power.

101.3 Intent.  This code shall regulate the design and construction of buildings for the use and conservation of energy over the life of each building. This code is intended to provide flexibility to permit the use of innovative approaches and techniques to achieve this objective. This code is not intended to abridge safety, health or environmental requirements contained in other applicable codes or ordinances. To the fullest extent feasible, use of modern technical methods, devices and improvements that tend to minimize consumption of energy without abridging reasonable requirements for the safety, health and security of the occupants or users of buildings shall be permitted. As far as may be practicable, the improvement of energy conservation construction practices, methods, equipment, materials and techniques shall be encouraged.

Nothing in this section or in any other provision of this code shall be construed to permit the commissioner to approve an application to waive, vary, modify or otherwise alter any provision of this code if such alteration would make such provision less restrictive than a standard or requirement of the ECCCNYS, unless the applicant has obtained approval for such alteration pursuant to Section 11-106 of the New York State Energy Law.

101.4 Applicability.  The provisions of this code shall apply to the construction of buildings. Where, in any specific case, different sections of this code specify different materials, methods of construction or other requirements, the most restrictive shall govern. Where there is a conflict between a general requirement and a specific requirement, the specific requirement shall govern.

101.4.1 Mixed occupancy. Where a building, having not more than three stories above grade plane, includes both commercial and residential occupancies, each occupancy shall be separately considered and shall meet the applicable provisions of Chapters C2, C3, C4 and C5 for commercial or the applicable provisions of the 2025 NYC ASHRAE 90.1, and Chapters R2, R3, R4, and R5 for residential.

101.5 Compliance. Commercial buildings shall comply with the provisions of this code applicable to commercial buildings. Residential buildings shall comply with the provisions of this code applicable to residential buildings.

101.5.1 Compliance software. Where chosen by the applicant, compliance with the NYCECC—Commercial Provisions or Residential Provisions, or portion thereof, or, if applicable, with the 2025 NYC ASHRAE 90.1 - can be demonstrated using; either of the following:

1. Computer software that is developed by the United States Department of Energy (such as COMcheck©), specifically for the NYCECC or, if applicable, specifically for the 2025 NYC ASHRAE 90.1, or

2. Other software expressly approved in writing by the New York Secretary of State as acceptable for demonstrating compliance with the NYCECC or, if applicable, for demonstrating compliance with the 2025 NYC ASHRAE 90.1.

101.5.1.1 Other analysis tools. Other performance analysis tools used to document simulated building performance for a specified application or limited scope in accordance with Section C407, are subject to the approval of the building official.

101.5.1.2 Mandatory provisions. The use of the software approach to demonstrate compliance with the commercial provisions, residential provisions, or 2025 NYC ASHRAE 90.1 as established by this code is not a defense for the failure to comply with any mandatory provision of this code. When using the software approach to demonstrate compliance with the provisions of  this code, compliance with all applicable mandatory provisions of this code is required.

101.5.2 Demonstration of compliance. For a building project application or applications required to be submitted to the department, the following documentation, as further described in the rules of the department, shall be required in order to demonstrate compliance with this code:

101.5.2.1 Professional statement. Any registered design professional or lead energy professional filing an application or applications for a new building or alteration project shall provide on a signed and sealed drawing a statement of compliance or exemption in accordance with the rules of the department.

101.5.2.2 Energy analysis. For any application that is not exempt from this code and for which a work permit is required in accordance with Section 28-105 of the Administrative Code, an energy analysis shall be provided on a sheet or sheets within the construction drawing set. The energy analysis shall identify the compliance path followed, demonstrate how the design complies with this code and be in a format as prescribed in the rules of the department. The energy analysis shall meet the requirements of this code for the entire project. Projects that utilize trade-offs among disciplines shall use DOE2-based energy modeling programs or other energy-modeling programs as prescribed in the rules of the department and shall be signed and sealed by a lead energy professional.

101.5.2.3 Supporting documentation. For any application that is not exempt from this code and for which a work permit is required in accordance with Section 28-105 of the Administrative Code, supporting documentation shall be required in the approved construction drawings.  See Section ECC 103 for further requirements.

SECTION ECC 102

ALTERNATE MATERIALS, METHOD OF CONSTRUCTION, DESIGN OR INSULATING SYSTEMS

102.1 General. This code is not intended to prevent the use of any material, method of construction, design or insulating system not specifically prescribed herein, provided that such material, method of construction, design or insulating system has been approved by the commissioner as (1) meeting the intent of this code, (2) achieving energy savings that are equivalent to or greater than would be achieved using prescribed materials, methods of construction, designs or insulating systems, and (3) meeting the requirements of Article 113 of Chapter 1 of Title 28 of the Administrative Code and the remaining New York City Construction Codes.

Nothing in this section shall be construed to permit the commissioner to approve an application that would waive, vary, modify, or otherwise alter any provision, standard, or requirement of this code if such alteration would make such provision less restrictive than a standard or requirement of the ECCCNYS unless the applicant has obtained approval for such alteration pursuant to Section 11-106 of the New York State Energy Law.

SECTION ECC 103

CONSTRUCTION DOCUMENTS

103.1 General. Construction documents shall be prepared in accordance with the provisions of Chapter 1 of Title 28 of the Administrative Code, the New York City Construction Codes, including this code, and the rules of the department.

103.2 Supporting documentation on construction documents. Supporting documentation shall include those construction documents that demonstrate compliance with this code.

103.2.1  Intent. Supporting documentation shall accomplish the following:

1.  Demonstrate conformance of approved drawings to the energy analysis for every element and value of the energy analysis;

2. Demonstrate conformance of approved drawings to other mandatory requirements of this code, including, but not limited to, sealing against air leakage from the building envelope and from ductwork as applicable, insulation of ducts and piping as applicable, mechanical and lighting controls with devices shown and operational narratives for each, and additional requirements as set forth in this section;

3. Identify required progress inspections in accordance with the scope of work, this code, the Administrative Code, the New York City Building Code and the rules of the department; and

4. Comply with other requirements as may be set forth in the rules of the department.

103.2.2 Detailed requirements. Construction documents shall be drawn to scale upon suitable material. Electronic media documents are permitted to be submitted in accordance with department procedures. Construction documents for a project shall be fully coordinated and of sufficient clarity to indicate the location, nature and extent of the work proposed, and show in sufficient detail pertinent data and features of the building, building systems and equipment as herein governed. Details shall include, but are not limited to, as applicable, the following:

1. Energy Code compliance path.

2. Insulation materials and their R-values.

3. Fenestration U-factors and solar heat gain coefficients (SHGCs).

4. Area-weighted average U-factor and solar heat gain coefficient (SHGC) calculations.

5. Air barrier and air sealing details, including the location of the air barrier.

6. Thermal bridges as identified in Section C402.7.

7. Mechanical system design criteria.

8. Mechanical and service water heating systems and equipment types, sizes and efficiencies.

9. Economizer description.

10. Equipment and system controls.

11. Fan motor horsepower (hp) and controls.

12. Duct sealing, duct and pipe insulation and location.

13. Lighting fixture schedule with wattage and control narrative.

14. Location of daylight zones on floor plans.

15. Location of pathways for routing of raceways or cable from the on-site renewable energy system to the electrical distribution equipment, where provided.

16. Location reserved for inverters, metering equipment and energy storage system (ESS), and a pathway reserved for routing of raceways or conduit from the on-site renewable energy system to the point of interconnection with the electrical service and the ESS, where provided.

17. Location and layout of a designated area for ESS, where provided.

18. Rated energy capacity and rated power capacity of the installed or planned ESS.

19. Location of designated EVSE spaces, EV ready spaces, and EV capable spaces in parking facilities and location of planned off-street loading spaces for future medium or heavy-duty EVSE.

20. Location of pathways for routing of raceways or cable from the enclosure or outlet of EV capable spaces to the electrical distribution equipment.

103.3 Examination of documents. In accordance with Article 104 of Chapter 1 of Title 28 of the Administrative Code, the department shall examine or cause to be examined the accompanying construction documents and shall ascertain by such examinations whether the construction indicated and described is in accordance with the requirements of this code and other pertinent laws, rules and regulations.

103.4 Changes during construction. For changes during construction refer to Section 28-104.3 of the Administrative Code.

SECTION ECC 104

INSPECTIONS

104.1 General. Except as otherwise specifically provided, inspections required by this code or by the department during the progress of work may be performed on behalf of the owner by an approved agency.  All inspections shall be performed at the sole cost and expense of the owner. Refer to Article 116 of Chapter 1 of Title 28 of the Administrative Code for additional provisions relating to inspections. In addition to any inspections otherwise required by this code or the rules of the department, the following inspections shall be required:

1.  Progress inspections. Progress inspections shall be performed in accordance with the rules of the department.

2. 	Final inspection. Refer to Article 116 of Chapter 1 of Title 28 of the Administrative Code and the rules of the department.

3. 	Issuance of Certificate of Compliance. Refer to Section 28-116.4.1 of the Administrative Code.

The requirements of this section shall not prohibit the operation of any heating equipment or appliances installed to replace existing heating equipment or appliances serving an occupied portion of a structure provided that a request for inspection of such heating equipment or appliances has been filed with the department not more than 48 hours after such replacement work is completed, and before any portion of such equipment or appliances is concealed by any permanent portion of the structure.

104.1.1 Approved agencies. Refer to Article 114 of Chapter 1 of Title 28 of the Administrative Code and the rules of the department.

104.1.2 Inspection of prefabricated construction assemblies. Prior to the issuance of a work permit for a prefabricated construction assembly having concealed mechanical work, the department shall require the submittal of an evaluation report by the manufacturer or approved agency on each prefabricated construction assembly, indicating the complete details of the mechanical system, including a description of the system and its components, the basis upon which the system is being evaluated for energy use, test results and similar information, and other data as necessary for the commissioner to determine conformance to this code.

104.1.2.1	Test and inspection records. Required test and inspection records shall be made available to the commissioner at all times during the fabrication of the mechanical system and the erection of the building; or such records as the commissioner designates shall be filed.

104.2 Testing. Envelope, heating, ventilating, air conditioning, service water heating, lighting and electrical systems shall be tested as required in this code and in accordance with Sections 104.2.1 through 104.2.3.  Except as otherwise required in this code or in the rules of the department, tests shall be made by the permit holder and witnessed by an approved agency.

104.2.1 New, altered, extended, renovated or repaired systems. New envelope, heating, ventilating, air conditioning, service water heating, lighting and electrical installations or systems, and parts of existing systems that have been altered, extended, renovated or repaired, shall be tested as prescribed herein or in the rules of the department to disclose leaks and defects.

104.2.2 Apparatus, instruments, material and labor for tests. Apparatus, instruments, material and labor required for testing an envelope, heating, ventilating, air conditioning, service water heating, lighting or electrical installation or system, or part thereof, shall be furnished by the permit holder.

104.2.3 Reinspection and testing. Where any work or installation does not pass an initial test or inspection, the necessary corrections shall be made so as to achieve compliance with the New York City Construction Codes, including this code. The work or installation shall then be reinspected or retested by the approved agency.

104.3 Sign-off of completed work. In addition to the requirements of Article 116 of Chapter 1 of Title 28 of the Administrative Code, Section 103.4 of this code and other requirements for sign-off, the project team shall either certify that construction does not differ from the last approved energy analysis or provide a whole-project as-built energy analysis and supporting documents, signed and sealed, for approval prior to sign-off. The as-built energy analysis and supporting documents shall reflect the materials, equipment and values actually used in the construction of the project, and shall demonstrate compliance of the constructed project with this code. Such signed and sealed documents may be accepted with less than full examination by the department based on the professional certification of the registered design professional.

104.4 Temporary connection. The commissioner shall have the authority to allow the temporary connection of an installation to the sources of energy for the purpose of testing the installation or for use under a temporary certificate of occupancy.

SECTION ECC 105

REFERENCED STANDARDS

105.1 Referenced standards. The standards referenced in Chapters C2, C3, C4, and C5 of this code shall be those that are listed in Chapter C6 of this code, and in the rules of the department and such standards shall be considered part of the requirements of the commercial provisions of this code to the prescribed extent of each such reference. The standards referenced in Chapters R2, R3, R4, and R5, of this code shall be those that are listed in Chapter R6 of this code, and in the rules of the department and such standards shall be considered part of the requirements of the residential provisions of this code to the prescribed extent of each such reference. The standards referenced in Appendix CA of this code shall be those that are listed in Section 12 of Appendix CA of this code, and in the rules of the department and such standards shall be considered part of the requirements of the commercial provisions of this code to the prescribed extent of each such reference. Where differences occur between provisions of this code and the referenced standards, the provisions of this code shall apply. Refer to Article 103 of Chapter 1 of Title 28 of the Administrative Code for additional provisions relating to referenced standards.

CHAPTER C2

DEFINITIONS

SECTION C201

GENERAL

Section C201.3 Words and terms defined in other codes.

Section C201.3 - Revise Section C201.3 to read as follows:

C201.3 Words and terms defined in other codes.  Where italicized words and terms are not defined in this code but are defined in the  New York City Building Code New York City Fire Code, New York City Fuel Gas Code, New York City Mechanical Code, New York City Plumbing Code,  such terms shall have the meanings ascribed to them in those codes.

Section C201.4 Words and terms not defined.

Section C201.4 - Revise Section C201.4 to read as follows:

C201.4 Words and terms not defined.  Where words and terms are not italicized or are italicized but not defined  in this publication or in the publications listed in Section C201.3, such words and terms shall have the meanings defined in applicable referenced standards, statutes, or regulations or shall have the ordinarily accepted meanings such as the context implies.

Section C202

GENERAL DEFINITIONS

Section C202 - Delete the definitions of “Building Code of New York State,” “Existing Building Code of New York State,” “Fire Code of New York State,” “Fuel Gas Code of New York State,” “Mechanical Code of New York State,” “Plumbing Code of New York State,” ”Property Maintenance Code of New York State,” “Residential Code of New York State,” and “Uniform Code.”

Section C202 – Add the definition of  “2025 NYC ASHRAE 90.1” after the definition of “2025 NYS ASHRAE 90.1.” to read as follows:

2025 NYC ASHRAE 90.1. New York City amendments to 2025 NYS ASHRAE 90.1

Section C202 – Delete the definition of  “Approval Or Approved,” “Approved Agency,”   after the definition of “Alteration.”

Section C202 – Add the definition of  “Approval Or Approved,” “Approved Agency,” after the definition of “Alteration.” to read as follows:

APPROVAL OR APPROVED. See Section 28-101.5 of the Administrative Code

APPROVED AGENCY. See Section 28-101.5 of the Administrative Code.

Section C202 – Delete the definition of  “Authority Having Jurisdiction,” after the definition of “Area-Weighted Average.”

Section C202 – Add the definition of  “Authority Having Jurisdiction,” after the definition of “Area-Weighted Average.” to read as follows:

AUTHORITY HAVING JURISDICTION. The governmental unit or agency responsible for administration and enforcement of the New York City Building Codes and NYCECC.

Section C202 – Delete the definition of  “Basement,”   after the definition of “Automobile Parking Space.”.

Section C202 – Add the definition of  “Basement Or Cellar, Energy Code,” after the definition of “Automobile Parking Space.” to read as follows:

BASEMENT OR CELLAR, ENERGY CODE. A story that is not a story above grade plane. See the definition of “Story above grade plane.”

Section C202 – Delete the definition of  “Building Entrance,” “Building Official,” after the definition of “Building Commissioning.”

Section C202 – Add the definition of  “Building Entrance,” “Building Official”     after the definition of “Building Commissioning.” to read as follows:

BUILDING ENTRANCE. Any doorway, set of doors, revolving door, vestibule, or other form of portal that is ordinarily used to gain access to the building or to exit from the building by its users and occupants. This does not include doors solely used to directly enter mechanical, electrical, and other building utility service equipment rooms.

BUILDING OFFICIAL. The Commissioner of Buildings of the City of New York or his or her duly authorized representative. See Section 28-101.5 of the Administrative Code.

Section C202 – Delete the definition of  “Building Thermal Envelope,”    after the definition of “Building System.”.

Section C202 – Add the definition of  “Building Thermal Envelope,”    after the definition of “Building System.” to read as follows:

BUILDING THERMAL ENVELOPE. The exterior walls, floors, slabs, ceilings, roofs, fenestration and any other building element assemblies (above and below grade) that enclose conditioned space or provide a boundary between conditioned space and unconditioned space.

Section C202 – Delete the definition of  “Chi-Factor (Χ-Factor),”    after the definition of “Character-Defining Features.”.

Section C202 – Add the definition of  “Chi-Factor (Χ-Factor),”    after the definition of “Character-Defining Features.” to read as follows:

CHI-FACTOR (χ-FACTOR). See “Thermal Bridge”.

Section C202 – Add the definition of  “Clear Field Thermal Bridge,” “Clear Field U-Factor,”       after the definition of “Clean Water Pump.” to read as follows:

CLEAR FIELD THERMAL BRIDGE. See “Thermal Bridge”.

CLEAR FIELD U-FACTOR. See “Thermal Bridge”.

Section C202 – Add the definition of  “Commissioner,” “Commissioning Plan,”       after the definition of “Commercial Building.” to read as follows:

COMMISSIONER. The commissioner of buildings of the city of New York, or his or her duly authorized representative.(See “Authority Having Jurisdiction” and “Building official”).

COMMISSIONING PLAN. See Section C408.2.1, Commissioning plan.

Section C202 – Delete the definition of  “Energy Code,”    after the definition of “Energy Analysis.”.

Section C202 – Add the definition of  “Energy Code,”    after the definition of “Energy Analysis.” to read as follows:

ENERGY CODE. The New York City Energy Conservation Code

Section C202 – Delete the definition of  “Fenestration,”    after the definition of “Fault Detection and Diagnostics (FDD) System.”

Section C202 – Add the definition of  “Fenestration,”    after the definition of “Fault Detection and Diagnostics (FDD) System.” to read as follows:

FENESTRATION. Products classified as either skylights or vertical fenestration.

Skylights. Glass units or other transparent or translucent glazing material installed at a slope of less than 60 degrees (1.05 rad) from horizontal, including unit skylights, tubular daylighting devices and glazing materials in solariums, sunrooms, roofs, greenhouses and sloped walls. A skylight includes the glazing assembly plus perimeter framing components.

Vertical fenestration. Windows units that are fixed or operable, doors that are more than half glazed, glazed block and combination opaque and glazed doors composed of glass or other transparent or translucent glazing materials and installed at a slope of not less than 60 degrees (1.05 rad) from horizontal.

Section C202 – Add the definition of  “Grade, Energy Finished,” “Grade Plane, Energy,”        after the definition of “General Lighting.” to read as follows:

GRADE, ENERGY FINISHED. The final top surface of lawns, walks, driveways, areaways or other non-vertical surfaces where the surface meets the foundation, slab edge or exterior wall of a building.

GRADE PLANE, ENERGY. A reference plane representing the average of finished ground level adjoining the building at exterior walls. Where the finished ground level slopes away from the exterior walls, the reference plane shall be established by the lowest points within the area between the building and the lot line or, where the lot line is more than 6 feet (1829 mm) from the building, between the building and a point 6 feet (1829 mm) from the building

Section C202 – Delete the definition of  “HVAC Total System Performance Ratio (HVAC TSPR),”    after the definition of “Humidistatic Controls.”

Section C202 – Add the definition of  “HVAC Total System Performance Ratio (HVAC TSPR),”    after the definition of “Humidistatic Controls.” to read as follows:

HVAC TOTAL SYSTEM PERFORMANCE RATIO (HVAC TSPR). The ratio of the sum of a building’s annual heating and cooling load in thousands of Btus to the sum of annual site energy consumption of the building HVAC systems in thousands of BTU.

Section C202 – Add the definition of  “Integrated Seasonal Coefficient Of Performance(ISCOP),” “INTEGRATED SEASONAL MOISTURE REMOVAL EFFICIENCY (ISMRE),”   after the definition of “Integrated Part Load Value (IPLV)” to read as follows:

INTEGRATED SEASONAL COEFFICIENT OF PERFORMANCE (ISCOP). A seasonal efficiency number that is a combined value based on the formula listed in AHRI Standard 920 of the two COP values for the heating season of a DX-DOAS unit water or air source heat pump, expressed in W/W.

INTEGRATED SEASONAL MOISTURE REMOVAL EFFICIENCY (ISMRE). A seasonal efficiency number that is a combined value based on the formula listed in AHRI Standard 920 of the four dehumidification moisture removal efficiency (MRE) ratings required for DX-DOAS units, expressed in lb of moisture/kWh.

Section C202 – Delete the definition of  “Labeled,”    after the definition of “Isolation Devices.”.

Section C202 – Add the definition of  “Labeled,”    after the definition of “Isolation Devices.” to read as follows:

LABELED. See Section 28-101.5 of the Administrative Code.

Section C202 – Add the definition of  “Lead Energy Professional,”    after the definition of “Large-Diameter Ceiling Fan.” to read as follows:

LEAD ENERGY PROFESSIONAL. The registered design professional who signs and seals the energy analysis for an entire project. Such individual may be the same registered design professional who signs and seals the design drawings for the same project.

Section C202 – Add the definition of  “Linear Thermal Bridge,”    after the definition of “Liquid Fuel.” to read as follows:

LINEAR THERMAL BRIDGE. See “Thermal Bridge”.

Section C202 – Delete the definition of  “Listed,”    after the definition of “Liner System (Ls).”.

Section C202 – Add the definition of  “Listed,”    after the definition of “Liner System (Ls).” to read as follows:

LISTED. See Section 28-101.5 of the Administrative Code.

Section C202 – Delete the definition of  “Market Value,”    after the definition of “Manual.”.

Section C202 – Add the definition of  “Moisture Removal Efficiency (MRE),”    after the definition of “Manual.” to read as follows:

MOISTURE REMOVAL EFFICIENCY (MRE). A ratio of the moisture removal capacity in pounds of moisture per hour to the power input values in kilowatts at any given set of standard rating conditions expressed in lb of moisture/kWh.

Section C202 – Add the definitions of  “Point Thermal Bridge,”   after the definition of “Physical Renewable Energy Power Purchase Agreement.” to read as follows:

POINT THERMAL BRIDGE. See “Thermal Bridge”.

Section C202 – Add the definitions of “Pre-Engineered Metal Building,”    “Professional Certification,”  “Project,”      after the definition of “Process Application.” to read as follows:

PRE-ENGINEERED METAL BUILDING. A pre-engineered metal building (PEMB) is a structure where the steel components—primary framing, secondary framing, and cladding—are designed and manufactured in a factory according to specific project requirements and then shipped to the construction site for assembly.

PROFESSIONAL CERTIFICATION. See Section 28-101.5 of the Administrative Code.

PROJECT. A design and construction undertaking comprised of work related to one or more buildings and the site improvements. A project is represented by one or more plan/work applications, including construction documents compiled in accordance with Section 107 of the New York City Building Code, that relate either to the construction of a new building or buildings or to the demolition or alteration of an existing building or buildings. Applications for a project may have different registered design professionals and different job numbers, and may result in the issuance of one or more permits.

Section C202 – Delete the definition of  “PSI-FACTOR (ψ-FACTOR),”    after the definition of “Proposed Design.”.

Section C202 – Add the definition of  “PSI-FACTOR (ψ-FACTOR),”    after the definition of “Proposed Design.” to read as follows:

PSI-FACTOR (ψ-FACTOR). See “Thermal Bridge”.

Section C202 – Delete the definitions of  “Standard Reference Design,”    after the definition of “Solar Heat Gain Coefficient (SHGC).”.

Section C202 – Add the definition of  “Spandrel Panel,”    after the definition of “Solar Heat Gain Coefficient (SHGC).” to read as follows:

SPANDREL PANEL. An opaque assembly within a fenestration framing system in a wall that is part of the building thermal envelope. Such panels are considered to be a portion of the opaque thermal envelope assembly.

Section C202 – Add the definitions of  “Story,” “Story Above Grade Plane,”    after the definition of “Storefront.” to read as follows:

STORY. The portion of a building included between the upper surface of a floor and the upper surface of the floor or roof next above. See the definitions of “Basement or Cellar, Energy Code and “Grade plane, Energy Code.” A story is measured as the vertical distance from top to top of two successive tiers of beams or finished floor surfaces and, for the topmost story, from the top of the floor finish to the top of the ceiling joists or, where there is not a ceiling, to the top of the roof rafters.

STORY ABOVE GRADE PLANE. Any story having its finished floor surface entirely above grade plane, or in which the finished surface of the floor next above is:

1. More than 6 feet (1829 mm) above average grade plane; or

2. More than 12 feet (3658 mm) above the finished ground level at any point.

Section C202 – Delete the definition of  “Thermal Bridge,”    after the definition of “Thermal Block”.

Section C202 – Add the definitions of  “Thermal Break Device,” “Thermal Bridge,” “    after the definition of “Thermal Block.” to read as follows:

THERMAL BREAK DEVICE. A pre-manufactured, load-bearing building component composed of multiple materials of differing thermal conductivities (e.g., steel, insulation, fiber-reinforced polymers) designed to structurally connect building elements while reducing thermal bridging. The thermal transmittance (U-value) or equivalent thermal conductivity (λeq) of such elements shall be determined using physical testing in accordance with ASTM C1363 or an approved equivalent calculation method. The calculated performance (U-value or equivalent thermal conductivity) shall include the effects of all embedded components through psi- or chi-value calculation methods.

THERMAL BRIDGE. An element or interface of elements that has higher thermal conductivity than the surrounding building thermal envelope, which creates a path of least resistance for heat transfer.

CHI-FACTOR (χ-FACTOR). The heat loss factor for a single thermal bridge characterized as a point element of a building thermal envelope (Btu/h x °F) [W/K].

CLEAR FIELD THERMAL BRIDGE. Elements of a building envelope assembly creating paths of decreased resistance for heat transfer which repeat at regular intervals, such as metal or wood studs, girts, and purlins.

CLEAR FIELD U-FACTOR. Thermal performance factor that accounts for clear field thermal bridge.

LINEAR THERMAL BRIDGE. a length-based element associated with horizontal, vertical, or diagonal elements that penetrates the insulation in the building thermal envelope and with a length measured along an exterior surface of the building thermal envelope, such as balconies, parapet-, roof-, floor-, or fenestration intersections, and shelf angles.

POINT THERMAL BRIDGE. An element that penetrates the insulation in the building thermal envelope, such as columns or beams passing through envelope assemblies, attachments, anchors, and connections not defined as clear field- or linear thermal bridges. The cross-sectional area is measured at the external surface of the outermost penetrated insulation layer.

PSI-FACTOR (ψ-FACTOR). The heat loss factor per unit length of a thermal bridge characterized as a linear element of a building thermal envelope (Btu/h x ft x °F) [W/(m x K)].

Section C202 – Delete the definitions of  “Wall, Above-Grade,”   “Wall, Below-Grade,”     after the definition of “Walk-In Freezer”.

Section C202 – Add the definitions of  “Wall, Above-Grade,”   “Wall, Below-Grade,”     after the definition of “Walk-In Freezer” to read as follows:

WALL, ABOVE-GRADE. A wall associated with the building thermal envelope that is more than 15 percent of the total surface area  above adjoining grade plane and is on the exterior of the building or any wall that is associated with the building thermal envelope that is not on the exterior of the building. This includes, but is not limited to, areaways below grade, between-floor spandrels, peripheral edges of floors, roof knee walls, dormer walls, gable end walls, walls enclosing a mansard roof, mechanical equipment penetrations and skylight shafts.

WALL, BELOW-GRADE. A wall associated with the basement or first story of the building that is part of the building thermal envelope, has not less than 85 percent of the total surface area below adjoining grade and is on the exterior of the building.

CHAPTER C3

GENERAL REQUIREMENTS

SECTION ECC C301

CLIMATE ZONES

Section C301.1 General.

Section C301.1 - Revise Section C301.1 to read as follows:

C301.1 General. For projects in the City of New York, Climate Zone 4A shall be used in determining the applicable requirements from Chapter C4.

SECTION C303

MATERIALS, SYSTEMS AND EQUIPMENT

Section C303.1.1 Building thermal envelope insulation.

Section C303.1.1 – Revise the Exception to Section C303.1.1 to read as follows:

Exception: For roof insulation installed above the deck, the R-value shall be labeled as required by the material standards specified in New York City Building Code.

Section C303.1.2 Insulation mark installation.

Section C303.1.2 – Revise the Exception to Section C303.12 to read as follows:

Exception: For roof insulation installed above the deck, the R-value shall be labeled as specified by the material standards in New York City Building Code.

Section C303.1.3 Fenestration product rating.

Section C303.1.3 - Revise Section C303.1.3 to read as follows:

C303.1.3 Fenestration product rating.  Fenestration product rating. U-factors, solar heat gain coefficient (SHGC), and visible transmittance (VT) of fenestration products shall be determined as follows:

1. For windows, doors and skylights, U-factor, SHGC and VT ratings shall be determined by a third party recognized by ANSI, ILAC or MiRa in accordance with NFRC 100 and NFRC 200.

2. Where required for garage doors and rolling doors, U-factor ratings shall be determined in accordance with either NFRC 100 or ANSI/DASMA 105.

U-factors, SHGC and VT shall be determined by accredited, independent laboratory, and certified by the manufacturer by a label affixed to the product or a label certificate specific to the products in the project.

Manufactured products or shop fabricated units lacking an affixed label shall be assigned a default U-factor from Table C303.1.3(1) or C303.1.3(2).. Products lacking  a label indicating SHGC or VT shall be assigned a default SHGC or VT from Table C303.1.3(3).

Where labeled or default values are not indicated, a signed and dated certificate showing compliance through modeling performed using Lawrence Berkley National Labs WINDOW/THERM software at the sizes and Boundary conditions prescribed in NFRC -100/200 shall be provided. The simulation shall be performed by a third-party recognized by ANSI, ILAC, MiRa. For Tubular Daylighting Devices, VTannual shall be measured and rated in accordance with NFRC 203.

Air infiltration rate shall be demonstrated by testing to ASTM E283, the test shall be conducted at an independent third-party laboratory recognized by ANSI, ILAC or MiRa, and shall be less than 5 years old

Section C303.1.5 Spandrel Panels.

Section C303.1.5 – Add new  Section C303.1.5 and Table C303.1.5 to read as follows:

C303.1.5 Spandrel Panels. U-factors of opaque assemblies within fenestration framing systems shall be determined in accordance with NFRC 100. U-factors shall be determined by an accredited, independent laboratory. Spandrel panels lacking a calculation shall be assigned a default U-factor from Table C303.1.5.

TABLE C303.1.5

DEFAULT EFFECTIVE U-FACTORS FOR SPANDREL PANELSa

| RATED R-VALUE OF INSULATION BETWEEN FRAMING MEMBERS |  | None | R-4 | R-7 | R-10 | R-15 | R-20 | R-25 | R-30 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| # Frame Type | Spandrel Panel | Default U-factor |  |  |  |  |  |  |  |
| Aluminum without thermal breakb | Single glass pane, stone, or metal panel | U-0.445 | ##### U-0.285 | U-0.259 | U-0.247 | ##### U-0.236 | U-0.230 | U-0.226 | U-0.224 |
|  | Double glazing with no low-e coatings | ###### U-0.356 | U-0.273 | U-0.254 | U-0.244 | U-0.234 | U-0.229 | U-0.226 | U-0.223 |
|  | Triple glazing or double glazing with low-e glass | U-0.313 | U-0.263 | U-0.249 | U-0.241 | U-0.233 | U-0.228 | U-0.225 | U-0.223 |
| Aluminum with thermal breakc | Single glass pane, stone, or metal panel | U-0.429 | U-0.243 | U-0.212 | U-0.197 | U-0.184 | U-0.176 | U-0.172 | U-0.169 |
|  | Double glazing with no low-e coatings | U-0.328 | U-0.228 | U-0.205 | U-0.193 | U-0.182 | U-0.175 | U-0.171 | U-0.168 |
|  | Triple glazing or double glazing with low-e glass | U-0.277 | U-0.217 | U-0.199 | U-0.189 | U-0.180 | U-0.174 | U-0.170 | U-0.167 |
| Structural glazingd | Single glass pane, stone, or metal panel | U-0.428 | U-0.217 | U-0.180 | U-0.161 | U-0.145 | U-0.136 | U-0.130 | U-0.126 |
|  | Double glazing with no low-e coatings | U-0.316 | U-0.199 | U-0.172 | U-0.157 | U-0.143 | U-0.135 | U-0.129 | U-0.126 |
|  | Triple glazing or double glazing with low-e glass | U-0.257 | U-0.186 | U-0.165 | U-0.152 | U-0.140 | U-0.133 | U-0.128 | U-0.125 |
| No framing or insulation is continuouse | Single glass pane, stone, or metal panel | ###### U-0.445 | U-0.160 | U-0.108 | U-0.082 | U-0.058 | U-0.045 | U-0.037 | U-0.031 |
|  | Double glazing with no low-e coatings | U-0.356 | U-0.147 | U-0.102 | U-0.078 | U-0.056 | U-0.044 | U-0.036 | U-0.030 |
|  | Triple glazing or double glazing with low-e glass | U-0.313 | U-0.139 | U-0.098 | U-0.076 | U-0.055 | U-0.043 | U-0.035 | U-0.030 |

a .Extrapolation outside of the table and interpolation between values in the table shall not be permitted. Assemblies with distance between framing less than 30 inches (762 mm), or not included in the default table, shall have a U-factor determined by testing in compliance with ASTM C1363 or modeling in compliance with ANSI/NFRC 100. Spandrel panel assemblies in the table do not include metal backpans. For designs with metal backpans, multiply the U-factor by 1.20. U-factors for spandrel panels include a 3/4 in. air gap and 5/8 in. gypsum board with R-value of 0.56 for the interior finish. The gypsum board is assumed to span between the window sill and a channel at the floor.

b. This frame type shall be used for systems that do not contain a non-metallic element that separates the metal exposed to the exterior from the metal that is exposed to the interior condition.

c. This frame type shall be used for systems where a urethane or other non-metallic element separates the metal exposed to the exterior from the metal that is exposed to the interior condition.

d. This frame type shall be used for systems that have no exposed mullion on the exterior.

e. This frame type shall be used for systems where there is no framing, or the insulation is continuous across and uninterrupted by the framing (also known as mullion wrap).

Section C303.2 Installation.

Section C303.2- Revise Section C303.2 to read as follows:

C303.2 Installation.   Materials, systems and equipment shall be installed in accordance with (i) the manufacturer’s  instructions and (ii) the applicable provisions of the New York City Construction Codes.

CHAPTER C4

COMMERCIAL ENERGY EFFICIENCY

SECTION C401

GENERAL

Section C401.2.1 ECCCNYS - Commercial Provisions.

Section C401.2.1 - Delete Section C401.2.1 in its entirety and add a new Section C401.2.1  to read as follows:

C401.2.1 New York City Energy Conservation Code.  Commercial Provisions. Commercial buildings shall comply with Sections C402 through C406 and C408. Dwelling units and sleeping units in Group R-2 buildings without systems serving multiple units shall be deemed to be in compliance with this chapter, provided that they comply with Section R406 .

Exception: Additions, alterations, repairs and changes of occupancy to existing buildings complying with Chapter C5.

Section C401.2.2 ASHRAE 90.1.

Section C401.2.2 - Delete Section C401.2.2 in its entirety and add a new Section C401.2.2  to read as follows:

C401.2.2 ASHRAE 90.1 Compliance Path.  Commercial buildings shall comply with the requirements of 2025 NYC ASHRAE 90.1 .

SECTION C402

BUILDING THERMAL ENVELOPE REQUIREMENTS

Table C402.1.2 Opaque Building Thermal Envelope Assembly Maximum Requirements, U-Factor Methoda, b

Revise Table C402.1.2 to read as follows:

TABLE C402.1.2

OPAQUE BUILDING THERMAL ENVELOPE ASSEMBLY MAXIMUM REQUIREMENTS, U-FACTOR METHODa, b

| CLIMATE ZONE | 4 |  | 5 |  | 6 |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | All other | Group R | All other | Group R | All other | Group R |
| Roofs |  |  |  |  |  |  |
| Insulation entirely above roof deck | U-0.030 | U-0.030 | U-0.030 | U-0.030 | U-0.028 | U-0.028 |
| Pre-engineered Metal buildings | U-0.035 | U-0.035 | U-0.035 | U-0.035 | U-0.028 | U-0.028 |
| Attic and other | U-0.020 | U-0.020 | U-0.020 | U-0.020 | U-0.017 | U-0.017 |
| Walls, above gradee |  |  |  |  |  |  |
| Massf | ## U-0.090 | ## U-0.080 | ## U-0.080 | ## U-0.071 | ## U-0.071 | ## U-0.067 |
| Pre-engineered Metal building | U-0.048 | U-0.048 | U-0.048 | U-0.048 | U-0.048 | U-0.046 |
| Metal framedi | ## U-0.061 | ## U-0.061 | ## U-0.052 | ## U-0.052 | ## U-0.47 | ## U-0.043 |
| Wood framed and other | ## U-0.061 | ## U-0.061 | ## U-0.048 | ## U-0.048 | ## U-0.048 | ## U-0.048 |
| ## Walls, below grade |  |  |  |  |  |  |
| Below-grade wallc | ## C-0.119 | C-0.092 | C-0.119 | C-0.092 | C-0.092 | C-0.063 |
| Floors |  |  |  |  |  |  |
| Massd | U-0.057 | U-0.051 | U-0.053 | U-0.051 | U-0.051 | U-0.051 |
| Joist/framing | U-0.033 | U-0.033 | U-0.033 | U-0.033 | U-0.027 | U-0.027 |
| Slab-on-grade floors |  |  |  |  |  |  |
| Unheated slabs | F-0.52 | F-0.52 | F-0.52 | F-0.51 | F-0.51 | F-0.434 |
| Heated slabs | ### F-0.62 | ### F-0.62 | ### F-0.62 | ### F-0.62 | ### F-0.62 | ### F-0.602 |
| Opaque doors |  |  |  |  |  |  |
| Nonswinging door | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 |
| Swinging doorg | ### U-0.37 | ### U-0.37 | ### U-0.37 | ### U-0.37 | ### U-0.37 | ### U-0.37 |
| Garage door <14% glazingh | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 | U-0.31 |

For SI: 1 pound per square foot = 4.88 kg/m2, 1 pound per cubic foot = 16 kg/m3.

a.	Where assembly U-factors, C-factors and F-factors are established in 2025 NYC ASHRAE 90.1, such opaque assemblies shall be a compliance alternative where those values meet the criteria of this table, provided that the construction, excluding the cladding system on walls, complies with the appropriate construction details from 2025 NYC ASHRAE 90.1.

b.	Where U-factors have been established by testing in accordance with ASTM C1363, such opaque assemblies shall be a compliance alternative where those values meet the criteria of this table. The R-value of continuous insulation shall be permitted to be added to or subtracted from the original tested design.

c.	Where heated slabs are below grade, below-grade walls shall comply with the U-factor requirements for above-grade mass walls.

d.	“Mass floors” shall be in accordance with Section C402.1.3.4.

e.	Reserved.

f.	 Mass walls” shall be in accordance with Section C402.1.3.4.

g.	Swinging door U-factors shall be determined in accordance with NFRC-100.

h.	Garage doors having a single row of fenestration shall have an assembly U-factor less than or equal to 0.44, provided that the fenestration area is not less than 14 percent and not more than 25 percent of the total door area.

i.	This refers to cold-formed steel studs or joists at 16” or 24” on-center

Section C402.1.2.1  Methods of determining U-, C- and F-factors.

Section C402.1.2.1  - Revise Section C402.1.2.1  to read as follows:

C402.1.2.1  Methods of determining U-, C- and F-factors.   Where assembly U-factors , C-factors and F-factors and calculation procedures are established in 2025 NYC ASHRAE 90.1 Appendix A for opaque assemblies, such opaque assemblies shall be a compliance alternative provided they meet the criteria of Table C402.1.2 and the construction, excluding cladding system on walls, complies with the applicable construction details from  2025 NYC ASHRAE 90.1 Appendix A.  Where U-factors have been established by testing in accordance with ASTM C1363, such opaque assemblies shall be a compliance alternative provided they meet the criteria of Table C402.1.4. The R-value of continuous insulation shall be permitted to be added to or subtracted from the original tested design  . Airspaces used for assembly evaluations shall comply with Section C402.2.7.

Section C402.1.2.1.6 Cold-formed steel assemblies.

Section C402.1.2.1.6 - Revise Section C402.1.2.1.6 to read as follows:

C402.1.2.1.6 Cold-formed steel assemblies. U-factors for building thermal envelopes containing cold-formed steel framed ceiling and walls shall be permitted to be determined in accordance with Table A3.3.3.1 in 2025 NYC ASHRAE 90.1. Where the steel-framed wall contains no cavity insulation and uses continuous insulation to satisfy the U-factor maximum, the steel-framed wall member spacing is permitted to be installed at any on-center spacing.

Section C402.1.2.1.7 Spandrel Panels.

Section C402.1.2.1.7 - Revise Section C402.1.2.1.7 to read as follows:

C402.1.2.1.7 Spandrel Panels. U-factors of opaque assemblies within fenestration framing systems shall be determined in accordance with ASTM C1363, ANSI/NFRC 100, or the default values in Table C303.1.5.

Table C402.1.2.1.7 Effective U-Factors For Spandrel Panelsa.

Table C402.1.2.1.7 - Delete Table C402.1.2.1.7 in its entirety.

Table C402.1.3 Opaque Building Thermal Envelope Insulation Component Minimum Requirements, R-Value Methoda

Revise Table C402.1.3 to read as follows:

TABLE C402.1.3

OPAQUE BUILDING THERMAL ENVELOPE INSULATION COMPONENT MINIMUM REQUIREMENTS, R-VALUE METHODa

| CLIMATE ZONE | 4 |  | 5 |  | 6 |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | All other | Group R | All other | Group R | All other | Group R |
| Roofs |  |  |  |  |  |  |
| Insulation entirely above roof deck | R-33ci | R-33ci | R-33ci | R-33ci | R-35ci | R-35ci |
| Pre-engineered Metal buildingsb | R-19ca + R-11 LS | R-19ca + R-11 LS | R-19ca + R-11 LS | R-19ca + R-11 LS | R-30ca + R-11 LS | R-25ca + R-11 + R-11 LS |
| Attic and other | R-53ca | R-53ca | R-53ca | R-53ca | R-60ca | R-60ca |
| Walls, above grade |  |  |  |  |  |  |
| Massf | R-13.3ci | R-13.3ci | R-13.3ci | R-15.2ci | R-15.2ci | R-17.5ci |
| Pre-engineered Metal building | R-13ca+14.9ci | R-13ca+14.9ci | R-13ca + R-14.9ci | R-13ca + R-14.9ci | R-13ca + R-14.9ci | R-13ca + R-15.8ci |
| Metal framedj | R-13ca+8.5ci | R-13ca +8.5ci | R-13ca+7.5ci | R-13ca+7.5ci | R-13ca+7.5ci | R-13ca+7.5ci |
| Wood framed and other | R-13ca+4.5ci or R-19ca+1.5ci | R-13ca+4.5ci or R-19ca+1.5ci | R-11 + R-10ci or R-19 + R-5ci or R-21 + R-4ci | R-11 + R-10ci or R-19 + R-5ci or R-21 + R-4ci | R-11 + R-10ci or R-19 + R-5ci or R-21 + R-4ci | R-11 + R-12ci or R-19 + R-7ci or R-21 + R-5ci |
| Walls, below grade |  |  |  |  |  |  |
| Below-grade walld | R-7.5ci | R-10ci | R-7.5ci | R-10ci | R-10ci | R-15ci |
| Floors |  |  |  |  |  |  |
| Masse | R-14.6ci | R-16.7ci | R-16.7ci | R-16.7ci | R-16.7ci | R-16.7ci |
| Joist/framing | R-30ca | R-30ca | R-30ca | R-30ca | R-38ca | R-38ca |
| Slab-on-grade floors |  |  |  |  |  |  |
| Unheated slabs | R-15 for 24″ below | R-15 for 24″ below | R-15 for 24″ below | R-20 for 24″ below | R-20 for 24″ below | R-20 for 48″ below |
| Heated slabsg | R-20 for 48" below + R-5 full slab | R-20 for 48" below + R-5 full slab | R-20 for 48″ below + R-5 full slab | R-20 for 48″ below + R-5 full slab | R-20 for 48″ below + R-5 full slab | R-15 full slab |

For SI: 1 inch = 25.4 mm, 1 pound per square foot = 4.88 kg/m2, 1 pound per cubic foot = 16 kg/m3.

ci = Continuous Insulation, NR = No Requirement, LS = Liner System, ca = Cavity insulation.

a.	Assembly descriptions can be found 2025 NYC ASHRAE 90.1 Appendix A.

b.	Where using R-value compliance method, a thermal spacer block shall be provided, otherwise use the U-factor compliance method in Table C402.1.2.

c.	 Reserved.

d.	Where heated slabs are below grade, below-grade walls shall comply with the exterior insulation requirements for heated slabs.

e.	“Mass floors” shall be in accordance with Section C402.1.3.4.

f.	“Mass walls” shall be in accordance with Section C402.1.3.4.

g.	The first value is for perimeter insulation and the second value is for full, under-slab insulation. Perimeter and full-slab insulation components shall be installed in accordance with Section C402.2.4.

h.    The first value is cavity insulation; the second value is continuous insulation. Therefore; “R-13ca+R-8.5ci” means R-13 cavity insulation and R-8.5 continuous insulation; “R-53ca” means R-53 cavity insulation and no continuous insulation.

i.    Where the required R-value in Table C402.1.3 is met by using continuous insulation such that cavity insulation is not required, the R-Value is applicable to any wall framing spacing.

j. This refers to cold-formed steel studs or joists at 16” or 24” on-center

Section C402.1.5 Rooms containing fuel-burning appliances

Section C402.1.5 – Revise the exception to Section C402.1.5 to read as follows:

Exception: Fireplaces and stoves complying the New York City Mechanical Code, and the fireplace blocking requirements of the New York City  Building Code.

Section C402.2.7 Airspaces.

Section C402.2.7 - Revise Section C402.2.7 to read as follows:

C402.2.7 Airspaces.  Where the R-value of an airspace is used to for compliance in accordance with Section C402.1, the airspace shall be enclosed in a cavity bounded on all sides by building components and constructed to minimize airflow into and out of the enclosed airspace. Airflow shall be deemed minimized where one of the following conditions occur:

1. The enclosed airspace is unventilated.

2. The enclosed airspace is bounded on at least one side by an anchored masonry veneer, constructed in accordance with Chapter 14 of the New York City Building Code and vented by veneer weep holes located only at the bottom of the airspace and spaced not less than 15 inches (381 mm) on center with top of the cavity airspace closed.

Exception: For ventilated cavities, the effect of ventilation of airspaces located on the exterior side of the continuous air barrier and adjacent to and behind the exterior wall-covering material shall be determined in accordance with ASTM C1363 modified with an airflow entering the bottom and exiting the top of the airspace at an air movement rate of not less than 70 mm/second.

Section C402.2.8 Fireplaces.

Section C402.2.8 - Revise Section C402.2.8 to read as follows:

C402.2.8 Fireplaces. New wood-burning fireplaces shall have tight-fitting flue dampers or doors, and outdoor combustion air as required by the fireplace construction provisions of the New York City Construction Codes, as applicable . Where using tight-fitting doors on factory-built fireplaces listed and labeled in accordance with UL 127, the doors shall be tested and listed for the fireplace.

Table C402.5 Building Envelope Fenestration Maximum U-Factor And SHGC Requirements

Revise Table C402.5 to read as follows:

TABLE C402.5

BUILDING ENVELOPE FENESTRATION MAXIMUM U-FACTOR

AND SHGC REQUIREMENTSc

| CLIMATE ZONE | 4 |  | 5 | 6 |
| --- | --- | --- | --- | --- |
|  | Vertical fenestration |  |  |  |
|  | U-factora |  |  |  |
|  | Below 95’d | Above 95’d |  |  |
| Metal framing, Fixed fenestration | U-0.30 | U-0.34 | U-0.34 | U-0.34 |
| Metal framing, Operable fenestration | U-0.40 | U-0.42 | U-0.43 | U-0.41 |
| Nonmetal framing, all fenestration | U-0.28 | U-0.28 | U-0.27 | U-0.27 |
| Entrance doors | U-0.63 |  | U-0.63 | U-0.63 |
|  | SHGCb |  |  |  |
| PF < 0.2 | 0.33 |  | 0.33 | 0.34 |
| 0.2 ≤ PF < 0.5 | 0.40 |  | 0.40 | 0.41 |
| PF ≥ 0.5 | 0.53 |  | 0.53 | 0.54 |
|  | Skylights |  |  |  |
| U-factor | U-0.48 |  | U-0.48 | U-0.48 |
| SHGCb | 0.38 |  | 0.38 | 0.38 |

- U-factor shall be rated in accordance with NFRC 100. U-factor shall reflect project-specific sizes, and include framing components plus glazing. SHGC shall be rated in accordance with NRFC 200.

- SHGC shall reflect project-specific sizes, and include framing components plus glazing. SHGC of the center-of-glass shall be an acceptable alternative for determining compliance with the SHGC requirements for the overall fenestration area.

- Fixed fenestration shall include glazed curtain walls, pre-fabricated storefronts and factory assembled fixed window units.

- Where a portion of the fenestration frame is installed at or above 95 feet above grade, the unit may meet the requirements for 95 feet and above.

Section C402.5.2 Minimum skylight fenestration area.

Section C402.5.2 -Revise the first paragraph of Section C402.5.2 to read as follows:

C402.5.2 Minimum skylight fenestration area.  Skylights shall be provided in enclosed spaces greater than 2,500 square feet (232 m2) in floor area, directly under a roof with not less than 75 percent of the ceiling area with a ceiling height greater than 15 feet (4572 mm), and used as an office, lobby, atrium, concourse, corridor, storage space, gymnasium/exercise center, convention center, automotive service area, space where manufacturing occurs, nonrefrigerated warehouse, retail store, distribution/sorting area, transportation depot, parking garage  , or workshop. The total toplit daylight zone shall be not less than half the floor area and shall comply with one of the following:

Section C402.5.3.4 Area-weighted U-factor.

Section C402.5.3.4 -Revise Section C402.5.3.4 to read as follows:

C402.5.3.4 Area-weighted U-factor.  An area-weighted average combining vertical fixed fenestration and vertical operable fenestration in accordance with Equation 4-4a shall be permitted to demonstrate compliance with the U-factor requirements for those categories in Table C402.5. Entrance door and skylight U-factors shall be permitted to be averaged separately by fenestration product category.  All U-factors shall be rated in accordance with NFRC 100.

∑[(U1 * A1) … (Un * An)] ≤ (Ufixed * Afixed + Uoperable * Aoperable) 	     (Equation 4-4a)

where:

U1 = rated U-factor of the 1st vertical fenestration assembly

A1 = area of the 1st vertical fenestration assembly

Un = rated U-factor of the nth vertical fenestration assembly

An = area of the nth vertical fenestration assembly

Ufixed = U-factor for vertical fixed fenestration in Table C402.4

Afixed = total area of the vertical fixed fenestration assemblies

Uoperable = U-factor for vertical operable fenestration in Table C402.4

Aoperable = total area of the vertical operable fenestration assemblies.

Section C402.6.2 Air leakage compliance.

Section C402.6.2 -Delete Section C402.6.2, Section C402.6.2.1, Section C402.6.2.2,Section C402.6.2.3, Section C402.6.2.3.1 and Section C402.6.2.3.2 in their entirety and add new C402.6.2, Section C402.6.2.1, Section C402.6.2.2, Section C402.6.2.2.1 and Section C402.6.2.2.2 to read as follows:

C402.6.2 Air leakage compliance.   Air leakage of the building thermal envelope shall be tested by an approved third party in accordance with Section C402.6.2.1 and C402.6.2.2. The measured air leakage shall not be greater than 0.35 cubic feet per minute per square foot (1.0 L/s x m2) of the building thermal envelope area at a pressure differential of 0.3 inch water gauge (75 Pa) with the calculated building thermal envelope surface area being the sum of the above- and below-grade building thermal envelope.

C402.6.2.1 Whole building test method and reporting.  The whole building  thermal envelope shall be tested by an approved third party in accordance with ASTM E779, ASTM E1827, ASTM E3158 or an equivalent approved method. Air leakage shall be measured following a multi-point regression method and then averaged from depressurization and pressurization tests. A report that includes the tested surface area, floor area, air by volume, stories above grade, and air leakage rates shall be submitted to the building official and the building owner

Exceptions:

1.	For buildings greater than 50,000 square feet (4,645 m2), portions of the building shall be permitted to be tested following the procedures for a guarded test in ASTM E3158 and the measured air leakage shall be area-weighted by the surface areas of the building thermal envelope in each portion. The weighted average tested air leakage shall not be greater than the whole building leakage limit. The following portions of the building shall be tested:

1.1	The entire building thermal envelope area of stories that have any conditioned spaces directly under a roof.

1.2	The entire building thermal envelope area of stories that have a building entrance,  a floor over unconditioned space,  a loading dock, or that are below grade.

1.3	Representative above-grade portions of the building totaling not less than 25 percent of the wall area enclosing the remaining conditioned space.

2. Hospital, Museums and other occupancies approved by the commissioner may be permitted to only perform pressurization test to comply with the requirements of this section.

C402.6.2.2 Building thermal envelope design and construction verification criteria. The installation of the continuous air barrier shall be verified by the building official, a registered design professional or approved agency in accordance with the following:

- A review of the construction documents and other supporting data shall be conducted to assess compliance with the requirements in Section C402.6.1.

- Inspection of continuous air barrier components and assemblies shall be conducted during construction to verify compliance with the requirements of Section C402.6.2.2.1 and C402.6.2.2.2. The air barrier shall remain accessible for inspection and repair.

- A final inspection report shall be provided for inspections completed by the registered design professional or approved agency. The inspection report shall be provided to the building owner or owner’s authorized agent and the building official. The report shall identify deficiencies found during inspection and details of corrective measures taken.

C402.6.2.2.1 Materials.  Materials with an air permeability not greater than 0.004 cfm/ft2 (0.02 L/s × m2) under a pressure differential of 0.3 inch water gauge (75 Pa) when tested in accordance with ASTM E2178 shall comply with this section. Materials in Items 1 through 16 shall be deemed to comply with this section, provided that joints are sealed and materials are installed as air barriers in accordance with the manufacturer’s instructions.

- Plywood with a thickness of not less than 3/8 inch (10 mm).

- Oriented strand board having a thickness of not less than 3/8 inch (10 mm).

- Extruded polystyrene insulation board having a thickness of not less than 1/2 inch (12.7 mm).

- Foil-back polyisocyanurate insulation board having a thickness of not less than 1/2 inch (12.7 mm).

- Closed-cell spray foam having a minimum density of 1.5 pcf (2.4 kg/m3) and having a thickness of not less than 1.5 inches (38 mm).

- Open-cell spray foam with a density between 0.4 and 1.5 pcf (6 and 2.4 kg/m3) and having a thickness of not less than 4.5 inches (113 mm).

- Exterior or interior gypsum board having a thickness of not less than 1/2 inch (12.7 mm).

- Cement board having a thickness of not less than 1/2 inch (12.7 mm).

- Built-up roofing membrane.

- Modified bituminous roof membrane.

- Single-ply roof membrane.

- A Portland cement/sand parge, or gypsum plaster having a thickness of not less than 5/8 inch (15.9 mm).

- Cast-in-place and precast concrete.

- Fully grouted concrete block masonry.

- Sheet steel or aluminum.

C402.6.2.2.2 Assemblies.  Assemblies of materials and components with an average air leakage not greater than 0.04 cfm/ft2 (0.2 L/s × m2) under a pressure differential of 0.3 inch of water gauge (75 Pa) where tested in accordance with ASTM E2357, ASTM E1677, ASTM D8052 or ASTM E283 shall comply with this section. Assemblies listed in Items 1 through 3 below shall be deemed to comply, provided that joints are sealed and the requirements of Section C402.6.1.2 are met.

- Concrete masonry walls coated with either one application of block filler or two applications of a paint or sealer coating.

- Masonry walls constructed of clay or shale masonry units with a nominal width of greater than or equal to 4 inches (102 mm) or more.

- A Portland cement/sand parge, stucco or plaster not less than 1/2 inch (12.7 mm) in thickness.

Section C402.6.4 Doors and access openings to shafts, chutes, stairways and elevator lobbies.

Section C402.6.4 -Revise Exceptions 1 and 2 from Section C402.6.4 to read as follows:

Exceptions:

1.	Door openings required to comply with the duct and air transfer opening requirements of the New York City Building Code.

2.	Doors and door openings required to comply with UL 1784 by the New York City Building Code.

Section C402.6.6 Vestibules.

Section C402.6.6 -Revise all the exceptions from Section C402.6.6 to read as follows:

Exceptions: Vestibules are not required for the following:

1.	Doors not intended to be used by the public, such as doors to mechanical or electrical equipment rooms, or intended solely for employee use.

2.	Doors opening directly from a sleeping unit or dwelling unit.

3.	Doors that open directly from a space less than 3,000 square feet (298 m2) in area, in buildings less than 75 feet (23 m) in height.

4.  Revolving doors.

5.	Doors used primarily to facilitate vehicular movement or material handling and adjacent personnel doors.

6.	Doors that open directly from a space less than 1,000 square feet (92.9  m2) in area, in buildings 75 feet (22.86  m) and greater in height.

Section C402.7 Thermal bridges in above-grade walls.

Section C402.7 -Delete Section C402.7, Section C402.7.1, Section C402.7.2,Section C402.7.3, Section C402.7.4 and Section C402.7.5 in their entirety and add new C402.7, Section C402.7.1, Section C402.7.2, Section C402.7.2.1, Section C402.7.2.2, Section C402.7.2.3, Section C402.7.2.4, Section C402.7.2.4.1, Section C402.7.2.5, to read as follows:

C402.7 Thermal bridging documentation and mitigation.  Where present, intersections listed in Section C402.7.1 that create thermal bridges shall be detailed in construction documents. Thermal bridges shall be mitigated in accordance with Section C402.7.2

Exceptions:

- Assemblies not enclosing conditioned space.

- Clear field thermal bridges.

- Thermal bridges in uninsulated assemblies.

- Linear- and point thermal bridges having a material thermal conductivity less than 3.0 Btu·in/h·ft2·°F (0.433 W/(m·K)).

- Alterations except as required under section C503

C402.7.1 Thermal bridge details.  The following intersections shall be evaluated for thermal bridges and be detailed in construction documents:

- Structural framing and members.

- Cladding attachment systems

- Assembly intersections:

  - Roof edge, parapet

  - Intermediate floor to wall intersection

  - Intermediate floor balcony or overhang to opaque wall intersection

  - Intermediate floor balcony in contact with vertical fenestration

  - Cladding support

  - Wall to vertical fenestration intersection

C402.7.2 Thermal bridges in above-grade walls.  Thermal bridges in above-grade walls shall comply with this section or an approved design accordance with Section 102.

Exceptions: Blocking, coping, flashing, and other similar materials for attachment of roof coverings.

C402.7.2.1 Balconies and floor decks.  Balconies and concrete floor decks shall not penetrate the building thermal envelope. Such assemblies shall be separately supported or shall be supported by structural attachments or elements that minimize thermal bridging through the building thermal envelope.

Exceptions: Balconies and concrete floor decks shall be permitted to penetrate the building thermal envelope where one of the following applies:

- An area-weighted U-factor is used for above-grade wall compliance which includes a U-factor of 0.8 Btu/h·ft2·°F (1.38W/m × K)  for the area of the above-grade wall penetrated by the concrete floor deck in accordance with Section C402.1.2.1.5, or

- An approved thermal break device with an R-value of not less than R-10 insulation material is installed in accordance with the manufacturer's instructions or.

- An approved design in accordance with Section 102 where the above-grade wall U-factor used for compliance accounts for all balcony and concrete floor deck thermal bridges.

C402.7.2.2 Cladding supports.  Linear elements supporting opaque cladding shall be offset from the structure with attachments that allow the continuous insulation, where present, to pass behind the cladding support element except at the point of attachment.

Exceptions:

1. An approved design in accordance with Section 102 where the above-grade wall U-factor used for compliance accounts for the cladding support element thermal bridge.

2. Anchoring for curtain wall and window wall systems where curtain wall and window wall systems comply with Section C402.7.2.4.

C402.7.2.3 Structural beams and columns.  Structural steel and concrete beams and columns that project through the building thermal envelope shall be covered with not less than R-5 insulation for not less than 2 feet (610 mm) beyond the interior or exterior surface of an insulation component within the building thermal envelope.

Exception:

1.Where an approved thermal break device is installed in accordance with the manufacturer's instructions.

2. An approved design in accordance with Section102 where the above-grade wall U-factor used to demonstrate compliance accounts for the beam or column thermal bridge .

C402.7.2.4 Vertical fenestration.  Vertical fenestration.  Vertical  fenestration intersections with above-grade walls shall comply with one or more of the following::

- Where above-grade walls include continuous insulation, the plane of the exterior glazing layer or, for metal frame fenestration, a non-metal thermal break in the frame shall be positioned within 2 inches (610 mm) of the interior or exterior surface of the continuous insulation.

- Where above-grade walls do not include continuous insulation, the plane of the exterior glazing layer or, for metal frame fenestration, a non-metal thermal break in the frame shall be positioned within the thickness of the integral or cavity insulation.

- The surface of the rough opening, not covered by the fenestration frame, shall be insulated with insulation of not less than R-3 material or covered with a wood buck that is not less than 1.5 inches (457 mm) thick.

Exceptions:

1. Where an approved design in accordance with Section 102 for the above-grade wall U-factor used for compliance accounts for thermal bridges at the intersection with the vertical fenestration.

2. Doors

C402.7.2.4.1 vertical fenestration with spandrels.  Vertical fenestration with spandrels shall comply with one of the following:

1.	For the intersection between vertical fenestration and opaque spandrel in a shared framing system, manufacturer's data for the spandrel U-factor shall account for thermal bridges.

2.	Use Default values as listed in C303.1.5

C402.7.2.5 Parapets.  Parapets shall comply with one or more of the following as applicable:

- Where continuous insulation is installed on the exterior side of the above-grade wall and the roof is insulated with insulation entirely above deck, the continuous insulation shall extend up both sides of the parapet not less than 2 feet (610 mm) above the roof covering or to the top of the parapet, whichever is less. Parapets that are an integral part of a fire-resistance rated wall, and the exterior continuous insulation applied to the parapet, shall comply with the fire resistance ratings of the building code.

- Where continuous insulation is installed on the exterior side of the above-grade wall and the roof insulation is below the roof deck, the continuous insulation shall extend up the exterior side of the parapet to not less than the height of the top surface of the roof assembly.

- Where continuous insulation is not installed on the exterior side of the above-grade wall and the roof is insulated with insulation entirely above deck, the wall cavity or integral insulation shall extend into the parapet up to the exterior face of the roof insulation or equivalent R-value insulation shall be installed not less than 2 feet (610 mm) horizontally inward on the underside of the roof deck.

- Where continuous insulation is not installed on the exterior side of the above-grade wall and the roof insulation is below the roof deck, the wall and roof insulation components shall be continuous and adjacent to each other at the roof-ceiling-wall intersection.

- Where a thermal break device with not less than R-10 insulation material aligned with the above-grade wall and roof insulation is installed in accordance with the manufacturer's instructions.

Exception: An approved design in accordance with Section 102 where the above-grade wall U-factor used for compliance accounts for the parapet thermal bridge.

SECTION C403

BUILDING MECHANICAL SYSTEMS

Section C403.2.2 Ventilation.

Section C403.2.2 – Revise Section C403.2.2 to read as follows:

C403.2.2 Ventilation.  Ventilation, either natural or mechanical, shall be provided in accordance with Chapter 4 of the New York City Mechanical Code. Where mechanical ventilation is provided, the system shall provide the capability to reduce the outdoor air supply to the minimum required by Chapter 4 of the   New York City Mechanical Code.

Section C403.3.4.1 Boiler oxygen concentration controls.

Section C403.3.4.1 – Delete the exception Section C403.3.4.1.

Section C403.3.5 Buildings with high efficiency space heating gas boiler systems.

Section C403.3.5 – Add new Section C403.3.5 to read as follows:

C403.3.5 Buildings with high efficiency space heating gas boiler systems.  New buildings where space heating is served by one or more gas hot water boilers with a minimum thermal efficiency (Et) of 90 percent when rated in accordance with the test procedures in Table C403.3.2(6) shall comply with this section, unless otherwise approved by the authority having jurisdiction. The hot water distribution system shall be designed so that the coils and other heat exchangers are selected such that at outdoor design conditions, the hot water return temperature entering the boilers is 120°F (49°C) or less when the boiler is firing.

Section C403.4.1.1 Heat pump supplementary heat.

Section C403.4.1.1 – Revise item 1 from  Section C403.4.1.1 to read as follows:

1.	The vapor compression cycle cannot provide necessary heating energy to satisfy the thermostat setting where controls are installed such that supplementary heat shall operate only when the outdoor air temperature is less than 17°F and supplemental heat capacity does not exceed 25 percent of total the design load.

Section C403.4.6 Demand responsive controls.

Section C403.4.6 – Revise item 2 from  Section C403.4.6 to read as follows:

2.	Automatically decreasing the zone operating heating set point by the following values: 1°F (0.5°C), 2°F (1°C), 3°F (1.5°C), and 4°F (2°C) while maintaining the minimum room temperature requirements of the New York City Building Code  .

Section C403.4.6 – Revise exception 1 and 2 from  Section C403.4.6 to read as follows:

1. Group I occupancies in accordance with the New York City Building Code.

2. Group H occupancies in accordance with the New York City Building Code.

Section C403.6.1 Variable air volume and multiple-zone systems.

Section C403.6.1 – Revise item 3 from  Section C403.6.1 to read as follows:

3.	The outdoor airflow rate required to meet the minimum ventilation requirements of Chapter 4 of the New York City  Mechanical Code.

Section C403.6.6 Multiple-zone VAV system ventilation optimization control.

Section C403.6.6 – Revise Section C403.6.6 to read as follows:

C403.6.6 Multiple-zone VAV system ventilation optimization control.  Multiple-zone VAV systems with direct digital control of individual zone boxes reporting to a central control panel shall have automatic controls configured to reduce outdoor air intake flow below design rates in response to changes in system ventilation efficiency (Ev) as defined by the New York City  Mechanical Code.

Exceptions:

1.	VAV systems with zonal transfer fans that recirculate air from other zones without directly mixing it with outdoor air, dual-duct dual-fan VAV systems, and VAV systems with fan-powered terminal units.

2.	Systems where total design exhaust airflow is more than 70 percent of total design outdoor air intake flow requirements.

Section C403.7.1 Demand control ventilation.

Section C403.7.1 – Revise Item 2 from Section C403.7.1 to read as follows:

2. Spaces larger than 250 square feet (23 m2) in Climate Zones 5 and  6 and spaces larger than 500 square feet (46.5 m2) in  climate zone 4 that have a design occupant load of 15 people or greater per 1,000 square feet (93 m2) of floor area, as established in New York City  Mechanical Code, and are served by systems with one or more of the following:

2.1 	 An air-side economizer

2.2 Automatic modulating control of the outdoor air damper.

2.3.	A design outdoor airflow greater than 3,000 cfm (1416 L/s).

Section C403.7.1 – Revise exception 5 from Section C403.7.1 to read as follows:

5.	Spaces with one of the following occupancy classifications as defined in the New York City Mechanical Code: correctional cells, education laboratories, barber, beauty and nail salons, and bowling alley seating areas.

Section C403.7.2 Parking garage ventilation controls.

Section C403.7.2 – Revise Section C403.7.2 to read as follows:

C403.7.2 Parking garage ventilation controls.  Ventilation systems employed in enclosed parking garages shall comply with New York City  Mechanical Code and the following:

1. Separate ventilation systems and control systems shall be provided for each parking garage section.

2. Control systems for each parking garage section shall be capable of and configured to reduce fan airflow to not less than 0.05 cfm per square foot [0.00025 m3 /(s × m2)] of the floor area served and not more than 20 percent of the design capacity.

3. The ventilation system for each parking garage section shall have controls and devices that result in fan motor demand of not more than 30 percent of design wattage at 50 percent of the design airflow.

Exception: Garage ventilation systems serving a single parking garage section having a total ventilation system motor nameplate horsepower (ventilation system motor nameplate kilowatt) not exceeding 5 hp (3.7 kW) at fan system design conditions and where the parking garage section has no mechanical cooling or mechanical heating.

Nothing in this section shall be construed to require more than one parking garage section in any parking structure.

Section C403.7.4.1 Nontransient dwelling units.

Section C403.7.4.1 – Revise Section C403.7.4.1 to read as follows:

C403.7.4.1 Nontransient dwelling units. Nontransient dwelling units shall  be provided with outdoor air energy recovery ventilation systems complying with one of the following:

1. The system shall have an enthalpy recovery ratio of not less than 50 percent at cooling design condition and not less than 60 percent at heating design condition.

2. The system shall have a sensible recovery efficiency (SRE) that is not less than 65 percent at 32°F (0°C). SRE shall be determined from a listed value or from interpolation of listed values at an airflow not less than the design airflow, based on testing in accordance with CAN/CSA C439.

Exception:

Enthalpy recovery ratio requirements at cooling design condition in Climate Zones 4, 5, and 6.

Section C403.7.4.2 Spaces other than nontransient dwelling units.

Section C403.7.4.2 – Revise Section C403.7.4.2 to read as follows:

C403.7.4.2 Spaces other than nontransient dwelling units.

Where the supply airflow rate of a fan system serving a space other than a nontransient dwelling unit exceeds the values specified in Tables C403.7.4.2(1) and C403.7.4.2(2), the system shall include  an energy recovery systementhalpy recovery ratio of not less than 50 percent, at design conditions. Where an air economizer is required, the energy recovery system shall include a bypass or controls that permit operation of the economizer as required by Section C403.5.

Exception: An energy recovery ventilation system shall not be required in any of the following conditions:

1.	Where energy recovery systems are prohibited by the Section 514.2 of the New York City Mechanical Code.

2.	Laboratory fume hood systems that include not fewer than one of the following features:

2.1. Variable-air-volume hood exhaust and room supply systems configured to reduce exhaust and makeup air volume to 50 percent or less of design values.

2.2. Direct makeup (auxiliary) air supply equal to or greater than 75 percent of the exhaust rate, heated not warmer than 2°F (1.1°C) above room setpoint, cooled to not cooler than 3°F (1.7°C) below room setpoint, with no humidification added, and no simultaneous heating and cooling used for dehumidification control.

3.	Systems serving spaces that are heated to less than 60°F (15.5°C) and that are not cooled.

4.	Heating and energy recovery where more than 60 percent of the outdoor heating energy is provided from site-recovered or site-solar energy in climate zones 5.

5.	Systems in climate zone 4 requiring dehumidification that employ series energy recovery and have a minimum SERR of 0.40.

6.Where the sum of the airflow rates exhausted and relieved within 30 feet of each other is less than 75 percent of the design ventilation outdoor air flow rate, excluding exhaust air that is any of the following:

a.	used for another energy recovery system,

b.	not allowed by ASHRAE Standard 170 for use in energy recovery systems with leakage potential,

c.	prohibited by the New York City Mechanical Code, or

d.	of Class 4 as defined in ASHRAE 62.1.

7.	Systems expected to operate less than 20 hours per week at the outdoor air percentage covered by Table C403.7.4.2(1).

8. Systems exhausting toxic, flammable, paint or corrosive fumes or dust.

9.	Commercial kitchen hoods used for collecting and removing grease vapors and smoke.

Section C403.7.5 Kitchen exhaust systems.

Section C403.7.5 – Revise exception 2 from Section C403.7.5 to read as follows:

2. Where allowed by the New York City  Mechanical Code, an energy recovery ventilation system is installed on the kitchen exhaust with a sensible heat recovery effectiveness of not less than 40 percent on not less than 50 percent of the total exhaust hood airflow.

Section C403.7.7 Shutoff dampers.

Section C403.7.7 – Revise Section C403.7.7 to read as follows:

C403.7.7 Shutoff dampers.  Outdoor air intake and exhaust openings and stairway and shaft vents shall be provided with Class I motorized dampers. The dampers shall have an air leakage rate not greater than 4 cfm/ft2 (20.3 L/s × m2) of damper surface area at 1.0 inch water gauge (249 Pa) and shall be labeled by an approved agency when tested in accordance with AMCA 500D for such purpose.

Outdoor air intake and exhaust dampers shall be installed with automatic controls configured to close when the systems or spaces served are not in use or during unoccupied period warm-up and setback operation, unless the systems served require outdoor or exhaust air in accordance with the New York City  Mechanical Code or the dampers are opened to provide intentional economizer cooling.

Stairway and elevator shaft vent dampers shall be installed with automatic controls configured to open upon the activation of any fire alarm initiating device of the building’s fire alarm system or the interruption of power to the damper, or by thermostatic control systems.

Exception: Nonmotorized gravity dampers shall be an alternative to motorized dampers for exhaust and relief openings as follows:

1.	In buildings less than three stories in height above grade plane.

2.	In buildings of any height located in Climate Zones 0, 1, 2 or 3.

3.	Where the design exhaust capacity is not greater than 300 cfm (142 L/s).

Nonmotorized gravity dampers shall have an air leakage rate not greater than 20 cfm/ft2 (101.6 L/s × m2) where not less than 24 inches (610 mm) in either dimension and 40 cfm/ft2 (203.2 L/s × m2) where less than 24 inches (610 mm) in either dimension. The rate of air leakage shall be determined at 1.0 inch water gauge (249 Pa) when tested in accordance with AMCA 500D for such purpose. The dampers shall be labeled by an approved agency.

Section C403.13.1 Duct and plenum insulation and sealing.

Section C403.13.1 – Revise Section C403.13.1 to read as follows:

C403.13.1 Duct and plenum insulation and sealing.  Supply and return air ducts and plenums shall be insulated with not less than R-6 insulation where located in unconditioned spaces and where located outside the building with not less than R-8 insulation in Climate Zone 4 and not less than R-12 insulation in Climate Zones 5 and 6. Ducts located underground beneath buildings shall be insulated as required in this section or have an equivalent thermal distribution efficiency. Underground ducts utilizing the thermal distribution efficiency method shall be listed and labeled to indicate the R-value equivalency. Where located within a building thermal envelope assembly, the duct or plenum shall be separated from the building exterior or unconditioned or exempt spaces by not less than R-8 insulation in Climate Zone 4 and not less than R-12 insulation in Climate Zones 5 and 6.

Exceptions:

1.	Where located within equipment.

2.	Where the design temperature difference between the interior and exterior of the duct or plenum is not greater than 15°F (8°C).

Ducts, air handlers and filter boxes shall be sealed. Joints and seams shall comply with the New York City  Mechanical Code.

Section C403.13.2 Duct construction.

Section C403.13.2 – Revise Section C403.13.2 to read as follows:

C403.13.2 Duct construction.  Ductwork shall be constructed and erected in accordance with the New York City Mechanical Code .

Section C403.13.2.1 Low-pressure duct systems.

Section C403.13.2.1 – Revise Section C403.13.2.1 to read as follows:

C403.13.2.1 Low-pressure duct systems.  Longitudinal and transverse joints, seams and connections of supply and return ducts operating at a static pressure less than or equal to 2 inches water gauge (w.g.) (498 Pa) shall be securely fastened and sealed with welds, gaskets, mastics (adhesives), mastic-plus-embedded-fabric systems or tapes installed in accordance with the manufacturer’s instructions. Pressure classifications specific to the duct system shall be clearly indicated on the construction documents in accordance with the New York City  Mechanical Code.

Exception: Locking-type longitudinal joints and seams, other than the snap-lock and button-lock types, need not be sealed as specified in this section.

Section C403.13.2.2 Medium-pressure duct systems.

Section C403.13.2.2 – Revise Section C403.13.2.2 to read as follows:

C403.13.2.2 Medium-pressure duct systems.  Ducts and plenums designed to operate at a static pressure greater than 2 inches water gauge (w.g.) (498 Pa) but less than 3 inches w.g. (747 Pa) shall be insulated and sealed in accordance with Section C403.12.1. Pressure classifications specific to the duct system shall be clearly indicated on the construction documents in accordance with the New York City  Mechanical Code.

Section C403.13.3 Piping insulation.

Section C403.13.3 – Revise Section C403.13.3 to read as follows:

C403.13.3 Piping insulation.  Piping serving as part of a heating or cooling system shall be thermally insulated in accordance with Table C403.13.3(1) or C403.13.3(2)..

Exceptions:

1.	Factory-installed piping within HVAC equipment tested and rated in accordance with a test procedure referenced by this code.

2.	Factory-installed piping within room fan-coils and unit ventilators tested and rated according to AHRI 440 (except that the sampling and variation provisions of Section 6.5 shall not apply) and AHRI 840, respectively.

3.	Piping that conveys fluids that have a design operating temperature range between 60°F (15°C) and 105°F (41°C).

4. Strainers, control valves, and balancing valves associated with piping 1 inch (25 mm) or less in diameter.

5. Direct buried piping that conveys fluids at or below 60°F (15°C).

6.In radiant heating systems, sections of piping intended by design to radiate heat.

SECTION C404

SERVICE WATER HEATING

Table C404.5.2.1 Internal Volume Of Various Water Distribution Tubing.

Table C404.5.2.1 – Delete Table C404.5.2.1 in it entirety and add new Table C404.5.2.1 to read as follows:

TABLE C404.5.2.1

INTERNAL VOLUME OF VARIOUS WATER DISTRIBUTION TUBING

| Nominal Size (inches) | Copper Type L | Copper Type K |
| --- | --- | --- |
| 3/8 | 0.97 | 0.84 |
| 1/2 | 1.55 | 1.45 |
| 3/4 | 3.22 | 2.90 |
| 1 | 5.49 | 5.17 |
| 11/4 | 8.36 | 8.09 |
| 11/2 | 11.83 | 11.45 |
| 2 | 20.58 | 20.04 |

For SI: 1 foot = 304.8 mm, 1 inch = 25.4 mm, 1 liquid ounce = 0.030 L, 1 oz/ft2 = 305.15 g/m2.

N/A = Not Available.

SECTION C405

ELECTRICAL POWER AND LIGHTING SYSTEMS

Section C405.1 General.

Section C405.1 – Revise Section C405.1 to read as follows:

C405.1 General. Electrical power and lighting systems and generation shall comply with this section. General lighting shall consist of all lighting included when calculating the total connected interior lighting power in accordance with Section C405.3.1 and which does not require specific application controls in accordance with Section C405.2.5.

Lighting controls shall be commissioned and completed in accordance with the requirements of Section C408.3 .

Exception: Dwelling units and sleeping units that comply with Section C405.2.10, Section C405.3.3 and Section C405.6.

Section C405.2.1 Occupant sensor controls.

Section C405.2.1 – Revise Section C405.2.1 to read as follows:

C405.2.1 Occupant sensor controls.  Occupant sensor controls shall be installed to control lights in the following space types:

1.	Classrooms/lecture/training rooms.

2. Computer Room, data center

3.	Conference/meeting/multipurpose rooms.

4.	Copy/print rooms.

5.	Lounges/breakrooms.

6. Cafeteria and fast food dinning areas.

7. Medical supply room in a healthcare facility.

8.	Enclosed offices.

9. Laundry/washing area.

10. Open plan office areas.

11. Restrooms.

12. Storage rooms.

13. Telemedicine room in a healthcare facility.

14. Locker rooms.

15.  Corridors/transition areas/stairways.

16.	 Warehouse storage areas.

17. Other spaces 300 square feet (28 m2) or less that are enclosed by floor-to-ceiling height partitions.

18. Janitorial closets.

Section C405.2.1.1 Occupant sensor control function.

Section C405.2.1.1 – Revise Section C405.2.1.1 to read as follows:

C405.2.1.1 Occupant sensor control function.  Occupant sensor controls in warehouses storage areas shall comply with Section C405.2.1.2. Occupant sensor controls in open plan office areas, cafeteria dining areas, and fast food dining areas, 300 square feet (28 m2) or greater in area shall comply with Section C405.2.1.3. Occupant sensor controls in corridors shall comply with Section C405.2.1.4. Occupant sensor control function for egress illumination shall comply with Section C405.2.1.5. Occupant sensor controls for all other spaces specified in Section C405.2.1 shall comply with the following:

1.	They shall automatically turn off lights within 15   minutes after all occupants have left the space.

2.	They shall be manual on or controlled to automatically turn on the lighting to not more than 50-percent power of full power.

3.	They shall incorporate a manual control to allow occupants to turn off lights.

Exceptions:

1.  Full automatic-on controls with no manual control shall be permitted in corridors, interior parking areas, stairways, restrooms, locker rooms, lobbies, library stacks and areas where manual operation would endanger occupant safety or security.

2.	Manual-on controls shall be required for classrooms (not including shop classrooms, laboratory classrooms, and preschool classrooms), conference/meeting rooms, employee lunch and break rooms, and offices smaller than 200 square feet (18.5 m2) in area. Such sensors and controls shall not have an override switch that converts from manual-on to automatic-on functionality, and may have a grace period of up to 30 seconds to turn on the lighting automatically after the sensor has turned off the lighting if occupancy is detected.

3.   Remote location of this local control device or devices shall be permitted for reasons of safety or security when each remote control device has an indicator pilot light as part of or next to the control device and the light is clearly labeled to identify the controlled lighting.

Section C405.2.1.2 Occupant sensor control function in warehouse storage areas.

Section C405.2.1.2 – Revise Item 2 from Section C405.2.1.2 to read as follows:

2.	Occupant sensors shall automatically reduce lighting power within each controlled area to an unoccupied setpoint of not more than 30 percent of full power within  15  minutes after all occupants have left the controlled area.

Section C405.2.1.3 Occupant sensor control function in open plan office areas.

Section C405.2.1.3 – Delete Section C405.2.1.3 in its entirety, add new Section C405.2.1.3  to read as follows:

C405.2.1.3 Occupant sensor control function in open plan office areas, cafeteria dining areas, and fast-food dining areas.  Occupant sensor controls in open plan office spaces, cafeteria dining areas, and fast-food dining areas less than 300 square feet (28 m2) in area shall comply with Section C405.2.1.1. Occupant sensor controls in all other open plan office spaces, cafeteria dining spaces, and fast food dining spaces shall comply with all of the following:

1.	The controls shall be configured so that general lighting can be separated into control zones with floor areas not greater than 600 square feet (55 m2) within the open plan office space or dining space. Where a through aisle traverses a control zone or separates two control zones, the luminaires serving the aisle shall be controlled separately from the general lighting in the control zones.

2.	General lighting in each control zone shall be permitted to automatically turn on upon occupancy within the control zone. General lighting in other unoccupied zones within the open plan office space shall be permitted to turn on to not more than 20 percent of full power or remain unaffected.

3.	The controls shall automatically turn off general lighting in all control zones within 15 minutes after all occupants have left the open plan office space.

Exception: Where general lighting is turned off by time-switch control complying with Section C405.2.2.1.

4.	General lighting in each control zone shall turn off or uniformly reduce lighting power to an unoccupied setpoint of not more than 20 percent of full power within  15  minutes after all occupants have left the control zone.

Section C405.2.1.4 Occupant sensor control function in corridors.

Section C405.2.1.4 – Revise Section C405.2.1.4 to read as follows:

C405.2.1.4 Occupant sensor control function in corridors. Occupant sensor controls in corridors shall uniformly reduce lighting power to an occupied setpoint not more than 50 percent of full power within  15   minutes after all occupants have left the space.

Exception: Corridors provided with less than two footcandles of illumination on the floor at the darkest point with all lights on.

Section C405.2.1.5 Occupant sensor control function for egress illumination.

Section C405.2.1.5 – Revise Section C405.2.1.5  to read as follows:

C405.2.1.5 Occupant sensor control function for egress illumination.  In new buildings, luminaires serving the exit access and providing means of egress illumination required by the New York City Building Code, including luminaires that function as both normal and emergency means of egress illumination, operating under normal conditions shall be controlled by a combination of listed emergency relay and occupancy sensors, or signal from another building control system, that automatically reduces the lighting power by at least 50%  percent when unoccupied for a period longer than 15 minutes.

Exceptions:

1.	Means of egress illumination serving the exit access that does not exceed 0.02 watts per square foot of building area is exempt from this requirement.

2. 	Emergency lighting designated to meet the requirements of the New York City Building Code .

Section C405.2.2.1 Time-switch control function.

Section C405.2.2.1 – Revise Item 7 from Section C405.2.2.1 to read as follows:

7. For spaces where schedules are not defined time switch controls are   programmed by default   to a schedule that turns off lights not less than 12 hours per day.

Section C405.2.4.1 Daylight-responsive control function.

Section C405.2.4.1 – Revise exceptions 1 and 2 from Section C405.2.4.1 to read as follows:

Exceptions:

1.	Within each space, up to 100    watts of lighting within the primary sidelit daylight zone is permitted to be controlled together with lighting in a primary sidelit daylight zone facing a different cardinal orientation.

2.	Within each space, up to 100 watts of lighting within the secondary sidelit daylight zone is permitted to be controlled together with lighting in a secondary sidelit daylight zone facing a different cardinal orientation.

Section C405.2.7.2 Building facade and landscape lighting.

Section C405.2.7.2 – Revise Section C405.2.7.2 to read as follows:

C405.2.7.2 Building facade and landscape lighting.  Building facade and landscape lighting shall automatically shut off, when sufficient daylight is present or not later than 1 hour after building or business closing to not earlier than 1 hour before building or business opening. For buildings that operate 24 hours, building’s façade lighting shall shut off at midnight.

Exception: Designated areas in zones 3 and 4 during special events may be permitted to extend hours of façade lighting at the discretion of the commissioner.

Section C405.2.9 Interior parking area.

Section C405.2.9  – Revise Item 1 from Section C405.2.9 to read as follows:

1.	Lighting power of each luminaire shall be automatically reduced by not less than 30 percent when there is no activity detected within a lighting zone for 15   minutes. Lighting zones for this requirement shall be not larger than 3,600 square feet (334.5 m2).

Section C405.2.9  – Revise Item 3 from Section C405.2.9 to read as follows:

3.	The power to luminaires within 20 feet (6096 mm) of perimeter wall openings or skylights  shall automatically reduce in response to daylight by at least 50 percent.

Section C405.2.10.1 Sleeping units and dwelling units in hotels, motels and vacation timeshare properties.

Section C405.2.10.1   – Revise Item 2 from Section C405.2.10.1 to read as follows:

2.	Lighting controls that automatically turn off all lighting and switched receptacles within 15   minutes after all occupants have left the unit.

Section C405.2.10.2 Sleeping units in congregate living facilities.

Section C405.2.10.2    – Revise Item 1 from  Section C405.2.10.2  to read as follows:

1.	Lighting in bathrooms shall be controlled by an occupant sensor control that automatically turns off lights within 15   minutes after all occupants have left the space.

Section C405.3.1 Total connected interior lighting power.

Section C405.3.1 – Revise exception 19 from  Section C405.3.1 to read as follows:

19. Lighting in dwelling units.

Section C405.3.2.1 Building Area Method.

Section C405.3.2.1     – Revise Item 2 from  Section C405.3.2.1 to read as follows:

2.	Determine the floor area for each building area type listed in Table C405.3.2(1) and multiply this area by the applicable value from Table C405.3.2(1) to determine the lighting power (watts) for each building area type. Dwelling units are excluded from lighting power allowance calculations by application of Section C405.3.3. The area of dwelling units is not included in the calculation.

Section C405.3.2.2 Space-by-Space Method.

Section C405.3.2.2      – Revise Item 2 from  Section C405.3.2.2  to read as follows:

2.	Determine the total floor area of all the spaces of each space type and multiply by the value for the space type in Table C405.3.2(2) to determine the allowed lighting power (watts) for each space type. Dwelling units are excluded from lighting power allowance calculations by application of Section C405.3.3. The area of dwelling units is not included in the calculation.

Table C405.3.2(1) Interior Lighting Power Allowances: Building Area Method.

Table C405.3.2(1)       – Revise Table C405.3.2(1) to read as follows:

TABLE C405.3.2(1)

INTERIOR LIGHTING POWER ALLOWANCES: 
BUILDING AREA METHOD

| BUILDING AREA TYPE | LPD (watts/ft2) |
| --- | --- |
| Automotive facility | 0.64 |
| Convention center | 0.64 |
| Courthouse | 0.74 |
| Dining: bar lounge/leisure | 0.69 |
| Dining: cafeteria/fast food | 0.66 |
| Dining: family | 0.61 |
| Dormitory | 0.52 |
| Exercise center | 0.65 |
| Fire station | 0.50 |
| Gymnasium | 0.67 |
| Health care clinic | 0.68 |
| Hospital | 0.86 |
| Hotel/Motel | 0.53 |
| Library | 0.78 |
| Manufacturing facility | 0.60 |
| Motion picture theater | 0.43 |
| Multiple-family | 0.46 |
| Museum | 0.56 |
| Office | 0.62 |

(continued)

TABLE C405.3.2(1)—continued

INTERIOR LIGHTING POWER ALLOWANCES: 
BUILDING AREA METHOD

| BUILDING AREA TYPE | LPD (watts/ft2) |
| --- | --- |
| Parking garage | 0.12 |
| Penitentiary | 0.65 |
| Performing arts theater | 0.82 |
| Police station | 0.62 |
| Post office | 0.62 |
| Religious building | 0.66 |
| Retail | 0.78 |
| School/university | 0.67 |
| Sports arena | 0.73 |
| Town hall | 0.67 |
| Transportation | 0.51 |
| Warehouse | 0.41 |
| Workshop | 0.83 |

For SI: 1 watt per square foot = 10.76 w/m2.

Table C405.3.2(2) Interior Lighting Power Allowances: Space-By-Space Method.

Table C405.3.2(2)       – Revise Table C405.3.2(2) to read as follows:

TABLE C405.3.2(2)

INTERIOR LIGHTING POWER ALLOWANCES: SPACE-BY-SPACE METHOD

| COMMON SPACE TYPESa | LPD (watts/ft)²) |
| --- | --- |
| Atrium |  |
| Less than 40 feet in height | 0.41 |
| Greater than 40 feet in height | 0.51 |
| Audience seating area |  |
| In an auditorium | 0.57 |
| In a gymnasium | 0.23 |
| In a motion picture theater | 0.27 |
| In a penitentiary | 0.28 |
| In a performing arts theater | 1.09 |
| In a religious building | 0.72 |
| In a sports arena | 0. 27 |
| Otherwise | 0.33 |
| Banking activity area | 0.56 |
| Breakroom (See Lounge/breakroom) |  |
| Classroom/lecture hall/training room |  |
| In a penitentiary | 0.74 |
| Otherwise | 0.72 |
| Computer room, data center | 0.75 |
| Conference/meeting/multipurpose room | 0.88 |
| Confinement cells | 0.52 |
| Copy/print room | 0.50 |
| Corridor |  |
| In a facility for the visually impaired (and not used primarily by the staff)b | 0.71 |
| In a hospital | 0.61 |
| Otherwise | 0.44 |
| Courtroom | 1.06 |
| Dining area |  |
| In bar/lounge or leisure dining | 0.62 |
| In cafeteria or fast food dining | 0.36 |
| In a facility for the visually impaired (and not used primarily by the staff)b | 1.22 |
| In family dining | 0.52 |
| In a penitentiary | 0.35 |
| Otherwise | 0.42 |
| Electrical/mechanical room | 0.39 |
| Emergency vehicle garage | 0.41 |
| Food preparation area | 0.92 |
| Guestroomc, d | 0.41 |
| Laboratory |  |
| In or as a classroom | 1.04 |
| Otherwise | 1.21 |
| Laundry/washing area | 0.43 |
| Loading dock, interior | 0.51 |
| Lobby |  |
| For an elevator | 0.52 |
| In a facility for the visually impaired (and not used primarily by the staff)b | 1.44 |
| In a motion picture theater | 0.20 |
| In a performing arts theater | 0.82 |
| Otherwise | 0.80 |
| Locker room | 0.43 |
| Lounge/breakroom |  |
| In a healthcare facility | 0.53 |
| Mother's wellness room | 0.68 |
| Otherwise | 0.44 |
| Office |  |
| Enclosed | 0.73 |
| Open plan | 0.56 |
| Parking area daylighting transition zone | 1.06 |
| Parking area, interiori | 0.11 |
| Pharmacy area | 1.23 |
| Restroom |  |
| In a facility for the visually impaired (and not used primarily by the staff b | 0.81 |
| Otherwise | 0.74 |
| Sales area | 0.85 |
| Seating area, general | 0.21 |
| Security screening general areas | 0.64 |
| Security screening in transportation facilities | 0.93 |
| Security screening transportation waiting area | 0.56 |
| Stairway (see Space containing stairway) |  |
| Stairwell | 0.47 |
| Storage room | 0.35 |
| Vehicular maintenance area | 0.53 |
| Workshop | 1.09 |
| BUILDING TYPE SPECIFIC SPACE TYPESa | LPD (watts/ft²) |
| Automotive (see Vehicular maintenance area) |  |
| Convention Center—exhibit space | 0.50 |
| Dormitory—living quartersc, d | 0.46 |
| Facility for the visually impairedb |  |
| In a chapel (and not used primarily by the staff) | 0.58 |
| In a recreation room (and not used primarily by the staff) | 1.20 |
| Gaming establishments |  |
| High limits game | 1.68 |
| Slots | 0.54 |
| Sportsbook | 0.82 |
| Table Games | 1.09 |
| Gymnasium/fitness center |  |
| In an exercise area | 0.50 |
| In a playing area | 0.75 |
| Healthcare facility |  |
| In an exam/treatment room | 1.16 |
| In an imaging room | 0.94 |
| In a medical supply room | 0.54 |
| In a nursery | 0.87 |
| In a nurse’s station | 0.75 |
| In an operating room | 1.87 |
| In a patient roomc | 0.45 |
| In a physical therapy room | 0.82 |
| In a recovery room | 0.89 |
| In a telemedicine room | 1.44 |
| Library |  |
| In a reading area | 0.77 |
| In the stacks | 1.18 |
| Manufacturing facility |  |
| In a detailed manufacturing area | 0.75 |
| In an equipment room | 0.61 |
| In an extra-high-bay area (greater than 50 feet floor-to-ceiling height) | 0.73 |
| In a high-bay area (25–50 feet floor-to-ceiling height) | 0.58 |
| In a low-bay area (less than 25 feet floor-to-ceiling height) | 0.61 |
| Museum |  |
| In a general exhibition area | 0.31 |
| In a restoration room | 0.77 |
| Performing arts theater—dressing room | 0.35 |
| Post office—sorting area | 0.66 |
| Religious buildings |  |
| In a fellowship hall | 0.50 |
| In a worship/pulpit/choir area | 0.75 |
| Retail facilities |  |
| In a dressing/fitting room | 0.45 |
| Hair salon | 0.65 |
| Nail salon | 0.75 |
| In a mall concourse | 0.57 |
| Massage space | 0.81 |
| Sports arena—playing area |  |
| For a Class I facility c | 2.26 |
| For a Class II facility d | 1.45 |
| For a Class III facility e | 1.08 |
| For a Class IV facility f | 0.72 |
| Transportation facility |  |
| Airport hanger | 1.36 |
| Passenger loading area | 0.71 |
| In a baggage/carousel area | 0.28 |
| In an airport concourse | 0.31 |
| At a terminal ticket counter | 0.40 |
| Warehouse—storage area |  |
| For medium to bulky, palletized items | 0.27 |
| For smaller, hand-carried items | 0.65 |

For SI: 1 foot = 304.8 mm, 1 watt per square foot = 10.76 w/m2.

a.	In cases where both a common space type and a building area specific space type are listed, the building area specific space type shall apply.

b.	A ‘Facility for the Visually Impaired’ is a facility that is licensed or will be licensed by local or state authorities for senior long-term care, adult daycare, senior support or people with special visual needs.

c.	Class I facilities consist of professional facilities; and semiprofessional, collegiate, or club facilities with seating for 5,000 or more spectators.

d.	Class II facilities consist of collegiate and semiprofessional facilities with seating for fewer than 5,000 spectators; club facilities with seating for between 2,000 and 5,000 spectators; and amateur league and high -school facilities with seating for more than 2,000 spectators.

e.	Class III facilities consist of club, amateur league and high -school facilities with seating for 2,000 or fewer spectators.

f.	Class IV facilities consist of elementary school and recreational facilities; and amateur league and high -school facilities without provision for spectators.

g.	The wattage of lighting in daylight transition zones and ramps without parking is excluded.

h.   Pool surfaces are excluded. Neither the surface area of the swimming or spa pool nor the wattage of the lighting serving them shall be counted.

Section C405.4 Horticultural lighting.

Section C405.4 – Revise Section C405.4 to read as follows:

C405.4 Horticultural lighting.  Permanently installed luminaires for horticultural lighting shall have a photosynthetic photon efficacy of not less than 2.1 micromoles per joule (μmol/J). Luminaires for horticultural lighting in greenhouses shall be controlled by a device that automatically turns off the luminaire when sufficient daylight is available. Luminaires for horticultural lighting shall be controlled by a device that automatically turns off the luminaire at specific programmed times.

Section C405.5.1 Total connected exterior lighting power.

Section C405.5.1 – Revise Exception 15 from Section C405.5.1 to read as follows

15. Lighting of the exterior means of egress as required by the New York City  Building Code.

Table C405.5.2(2) Lighting Power Allowances For Building Exteriors.

Table C405.5.2(2) – Revise Table C405.5.2(2) to read as follows:

TABLE C405.5.2(2)

LIGHTING POWER ALLOWANCES FOR BUILDING EXTERIORS

|  | LIGHTING ZONES |  |  |  |
| --- | --- | --- | --- | --- |
|  | Zone 1 | Zone 2 | Zone 3 | Zone 4 |
| Base Site Allowance | 160 W | 280 W | 400 W | 560 W |
| Uncovered Parking Areas |  |  |  |  |
| Parking area, exterior | 0.015 W/ft2 | 0.026 W/ft2 | 0.037 W/ft2 | 0.05 W/ft2 |
| Building Grounds |  |  |  |  |
| Walkways and ramps | 0.50 W/linear foot | 0.50 W/linear foot | 0.55 W/linear foot | 0.60 W/linear foot |
| Plaza areas | 0.028 W/ft2 | 0.049 W/ft2 | 0.070 W/ft2 | 0.098 W/ft2 |
| Dining areas | 0.156 W/ft2 | 0.273 W/ft2 | 0.390 W/ft2 | 0.546 W/ft2 |
| Stairways | Exempt | Exempt | Exempt | Exempt |
| Pedestrian tunnels | 0.063 W/ft2 | 0.110 W/ft2 | 0.157 W/ft2 | 0.220 W/ft2 |
| Landscaping | 0.014 W/ft2 | 0.025 W/ft2 | 0.036 W/ft2 | 0.04 W/ft2 |
| Building Entrances and Exits |  |  |  |  |
| Pedestrian and vehicular entrances and exits | 5.6 W/linear foot of opening | 9.8 W/linear foot of opening | 14 W/linear foot of opening | 19.6 W/linear foot of opening |
| Entry canopies | 0.072 W/ft2 | 0.126 W/ft2 | 0.180 W/ft2 | 0.252W/ft2 |
| Loading docks | 0.104 W/ft2 | 0.182 W/ft2 | 0.260 W/ft2 | 0.35 W/ft2 |
| Sales Canopies |  |  |  |  |
| Free-standing and attached | 0.20 W/ft2 | 0.35 W/ft2 | 0.50 W/ft2 | 0.70 W/ft2 |
| Outdoor Sales |  |  |  |  |
| Open areas (including vehicle sales lots) | 0.072 W/ft2 | 0.126 W/ft2 | 0.180 W/ft2 | 0.252 W/ft2 |
| Street frontage for vehicle sales lots in addition to “open area” allowance | No allowance | 7 W/linear foot | 7 W/linear foot | 14.4 W/linear foot |

For SI: 1 foot = 304.8 mm, 1 watt per square foot = W/0.0929 m2.

W = watts.

Section C405.6  Dwelling electrical meter.

Section C405.6  – Delete Section C405.6  in its entirety, add new Section C405.6, Section C405.6.1 and C405.6.2    to read as follows:

C405.6 Electrical meter. Electrical service within buildings shall comply with the following:

C405.6.1   Dwelling electrical meter.  Each dwelling unit located in a Group R-2 building shall have a separate electrical meter.

C405.6.2 Electrical meters for tenant spaces in covered buildings. Each covered tenant space in a new building shall be equipped with a separate meter or sub-meter to measure the electrical consumption of such space when let or sublet. The terms covered building, meter, sub-meter, tenant space and covered tenant space shall have the same meanings as defined in Section 28-311.2 of the NYC Administrative Code.

Section C405.10.1 Elevator cabs.

Section C405.10.1 – Delete Section C405.10.1 in its entirety, add new Section C405.10.1, Section C405.10.1.1, Section C405.10.1.1.1, Section C405.10.1.1.2 and Section C405.10.1.1.3   to read as follows:

C405.10.1 Elevator equipment and cabs. For the luminaires in each elevator cab, not including signals and displays, the sum of the lumens divided by the sum of the watts shall be not less than 35 lumens per watt. Ventilation fans in elevators that do not have their own air-conditioning system shall not consume more than 0.33 watts/cfm at the maximum rated speed of the fan. Controls shall be provided that will de-energize ventilation fans and lighting systems when the elevator is stopped, unoccupied and with its doors closed for over 15 minutes.

C405.10.1.1 Power conversion system. New traction elevators with a rise of 75 feet (23 m) or more in new buildings shall have a power conversion system that complies with Sections C405.10.1.1.1 through C405.10.1.1.3.

C405.10.1.1.1 Motor. Induction motors with a Class IE2 efficiency rating, as defined by IEC EN 60034-30, or alternative technologies, such as permanent magnet synchronous motors that have equal or better efficiency, shall be used.

C405.10.1.1.2 Transmission.  Transmissions shall not reduce the efficiency of the combined motor/transmission below that shown for the Class IE2 motor for elevators with capacities below 4,000 pounds (1814 kg). Gearless machines shall be assumed to have a 100 percent transmission efficiency.

C405.10.1.1.3 Drive. Potential energy released during motion shall be recovered with a regenerative drive that supplies electrical energy to the building electrical system.

Section C405.12 Automatic receptacle control.

Section C405.12- Delete Section C405.12, C405.12.1 in their entirety.

Section C405.13 Energy monitoring.

Section C405.13-  Delete Section C405.13,  Section C405.13.1, Section C405.13.2, Table C405.13.2, Section C405.13.3, Section C405.13.4, Section C405.13.5, Section C405.13.6, Section C405.13.7, Section C405.13.8, Table C405.13.8, Section C405.13.9, Section C405.13.10 and Section C405.13.11, Section C405.14in their entirety.

Section C405.12 Commercial kitchen equipment.

Section C405.12 – Add new Section C405.12, Table C405.12(1), Table C405.12(2), Table C405.12(3), Table C405.12(4) and Table C405.12(5)to read as follows:

C405.12 Commercial kitchen equipment.

Commercial kitchen equipment shall comply with the minimum efficiency requirements of Tables C405.12(1)  through C405.12(5).

TABLE C405.12(1)

MINIMUM EFFICIENCY REQUIREMENTS: COMMERCIAL FRYERS

(This table is intended to be a restatement of the legally binding provisions found in Title 10 CFR Part 431 included here as a convenience to the users of this code)

|  | HEAVY-LOAD COOKING ENERGY EFFICIENCY | IDLE ENERGY RATE | TEST PROCEDURE |
| --- | --- | --- | --- |
| Standard Open Deep-Fat Gas Fryers | ≥ 50% | ≤ 9,000 Btu/hr | ASTM Standard F1361- 17 |
| Standard Open Deep-Fat Electric Fryers | ≥ 83% | ≤ 800 watts |  |
| Large Vat Open Deep- Fat Gas Fryers | ≥ 50% | ≤ 12,000 Btu/hr | ASTM Standard F2144- 17 |
| Large Vat Open Deep- Fat Electric Fryers | ≥ 80% | ≤ 1,100 watts |  |

TABLE C405.12(2)

MINIMUM EFFICIENCY REQUIREMENTS: COMMERCIAL HOT FOOD HOLDING CABINETS

(This table is intended to be a restatement of the legally binding provisions found in Title 10 CFR Part 431 included here as a convenience to the users of this code)

| PRODUCT INTERIOR VOLUME (CUBIC FEET) | MAXIMUM IDLE ENERGY CONSUMPTION RATE (WATTS) | TEST PROCEDURE |
| --- | --- | --- |
| 0 < V < 13 | ≤ 21.5 V | ASTM Standard F2140-11 |
| 13 ≤ V < 28 | ≤ 2.0 V + 254.0 |  |
| 28 ≤ V | ≤ 3.8 V + 203.5 |  |

TABLE C405.12(3)

MINIMUM EFFICIENCY REQUIREMENTS: COMMERCIAL STEAM COOKERS

(This table is intended to be a restatement of the legally binding provisions found in Title 10 CFR Part 431 included here as a convenience to the users of this code)

| FUEL TYPE | PAN CAPACITY | COOKING ENERGY EFFICIENCYa | IDLE RATE | TEST PROCEDURE |
| --- | --- | --- | --- | --- |
| Electric Steam | 3-pan | 50% | 400 watts | ASTM Standard F1484-18 |
|  | 4-pan | 50% | 530 watts |  |
|  | 5-pan | 50% | 670 watts |  |
|  | 6-pan and larger | 50% | 800 watts |  |
| Gas Steam | 3-pan | 38% | 6,250 Btu/h |  |
|  | 4-pan | 38% | 8,350 Btu/h |  |
|  | 5-pan | 38% | 10,400 Btu/h |  |
|  | 6-pan and larger | 38% | 12,500 Btu/h |  |

a.	Cooking Energy Efficiency is based on heavy load (potato) cooking capacity.

TABLE C405.12(4)

MINIMUM EFFICIENCY REQUIREMENTS: COMMERCIAL DISHWASHERS

(This table is intended to be a restatement of the legally binding provisions found in Title 10 CFR Part 431 included here as a convenience to the users of this code)

| MACHINE TYPE | HIGH TEMP EFFICIENCY REQUIREMENTS |  | LOW TEMP EFFICIENCY REQUIREMENTS |  | TEST PROCEDURE |
| --- | --- | --- | --- | --- | --- |
|  | Idle Energy Ratea | Water Consumptionb | Idle Energy Ratea | Water Consumptionb |  |
| Under Counter | ≤ 0.50 kW | ≤ 0.86 GPR | ≤ 0.50 kW | ≤ 1.19 GPR |  |
| Stationary |  |  |  |  |  |
| Single Tank | ≤ 0.70 kW | ≤ 0.89 GPR | ≤ 0.60 kW | ≤ 1.18 GPR | ASTM F1696- |
| Door |  |  |  |  | 18 |
| Pot, Pan , and | ≤ 1.20 kW | ≤ 0.58 GPSF | ≤ 1.00 kW | ≤ 0.58 GPSF |  |
| Utensil |  |  |  |  |  |
| Single Tank | ≤ 1.50 kW | ≤ 0.70 GPR | ≤ 1.50 kW | ≤ 0.79 GPR |  |
| Conveyor |  |  |  |  |  |
| Multiple Tank | ≤ 2.25 kW | ≤ 0.54 GPR | ≤ 2.00 kW | ≤ 0.54 GPR |  |
| Conveyor |  |  |  |  | ASTM F1920- |
| Single Tank | Reported | GPH ≤ 2.975x + | Reported | GPH ≤ 2.975x + | 15 |
| Flight Type |  | 55.00 |  | 55.00 |  |
| Multiple Tank | Reported | GPH ≤ 4.96x + | Reported | GPH ≤ 4.96x + |  |
| Flight Type |  | 17.00 |  | 17.00 |  |

a.	Idle results shall be measured with the door closed and represent the total idle energy consumed by the machine including all tank heater(s) and controls. Booster heater (internal or external) energy consumption should not be part of this measurement unless it cannot be separately monitored per US EPA Energy Star Commercial Dishwasher Specification Version 2.0.

b.	GPR = gallons per rack; GPSF = gallons per square foot of rack; GPH = gallons per hour; x = sf of conveyer belt (i.e., W*L)/min (maximum conveyor speed

TABLE C405.12(5)

MINIMUM EFFICIENCY REQUIREMENTS: COMMERCIAL OVENS

(This table is intended to be a restatement of the legally binding provisions found in Title 10 CFR Part 431 included here as a convenience to the users of this code)

| FUEL TYPE | CLASSIFICATION | IDLE RATE | COOKING-ENERGY EFFICIENCY, % | TEST PROCEDURE |
| --- | --- | --- | --- | --- |
| Convection Ovens |  |  |  |  |
| Gas | Full-Size | ≤ 12,000 Btu/h | ≥ 46 | ASTM F1496 - 13 |
| Electric | Half-Size | ≤ 1.0 Btu/h | ≥ 71 |  |
|  | Full-Size | ≤ 1.60 Btu/h |  |  |
| Combination Ovens |  |  |  |  |
| Gas | Steam Mode | ≤ 200Pa + 6,511 Btu/h | ≥ 41 | ASTM F2861 - 17 |
|  | Convection Mode | ≤ 150Pa + 5,425 Btu/h | ≥ 56 |  |
| Electric | Steam Mode | ≤ 0.133Pa + 0.6400 kW | ≥ 55 |  |
|  | Convection Mode | ≤ 0.080Pa + 0.4989 kW | ≥ 76 |  |
| Rack Ovens |  |  |  |  |
| Gas | Single | ≤ 25,000 Btu/h | ≥ 48 | ASTM F2093 - 18 |
|  | Double | ≤ 30,000 Btu/h | ≥ 52 |  |

a.	P = Pan Capacity: The number of steam table pans the combination oven is able to accommodate as per the ASTM F1495–05 standard specification.

Section C405.13 Automatic receptacle control.

Section C405.13 – Add new Section C405.13 and  C405.13.1 to read as follows:

C405.13 Automatic receptacle control.

The following shall have automatic receptacle control complying with Section C405.13.1:

- At least 50 percent of all 125V, 15- and 20-amp receptacles installed in enclosed offices, conference rooms, rooms used primarily for copy or print functions, breakrooms, classrooms and individual workstations, including those installed in modular partitions and module office workstation systems.

- At least 25 percent of branch circuit feeders installed for modular furniture not shown on the construction documents.

C405.13.1 Automatic receptacle control function.

Automatic receptacle controls shall comply with the following:

1.	Either split controlled receptacles shall be provided with the top receptacle controlled, or a controlled receptacle shall be located within 12 inches (304.8 mm) of each uncontrolled receptacle.

2.	One of the following methods shall be used to provide control:

2.1.	A scheduled basis using a time-of-day operated control device that turns receptacle power off at specific programmed times and can be programmed separately for each day of the week. The control device shall be configured to provide an independent schedule for each portion of the building of not more than 5,000 square feet (464.5 m2) and not more than one floor. The occupant shall be able to manually override an area for not more than 2 hours. Any individual override switch shall control the receptacles in a portion of the building not more than 5,000 feet (1524 m).

2.2.	An occupant sensor control that shall turn off receptacles within 15 minutes of all occupants leaving a space.

2.3.	An automated signal from another control or alarm system that shall turn off receptacles within  15 minutes after determining that the area is unoccupied.

3.	All controlled receptacles shall be permanently marked in accordance with NFPA 70 and be uniformly distributed throughout the space.

4.	Plug-in devices shall not comply.

Exceptions: Automatic receptacle controls are not required for the following:

1.	Receptacles specifically designated for equipment requiring continuous operation (24 hours per day, 365 days per year).

2.	Spaces where an automatic control would endanger the safety or security of the room or building occupants.

3.	Within a single modular office workstation, noncontrolled receptacles are permitted to be located more than 12 inches (304.8 mm), but not more than 72 inches (1828 mm) from the controlled receptacles serving that workstation.

Section C405.14 Energy monitoring.

Section C405.14 – Add new Section C405.14,  Section C405.14.1, Section C405.14.2, Table C405.14.2, Section C405.14.3, Section C405.14.4, Section C405.14.5, Section C405.14.6, Section C405.14.7, Section C405.14.8, Table C405.14.8, Section C405.14.9, Section C405.14.10 and Section C405.14.11  to read as follows:

C405.14 Energy monitoring.

New buildings with a gross conditioned floor area of 10,000 square feet (929 m2) or larger shall be equipped to measure, monitor, record and report energy consumption in accordance with Sections C405.14.1 through C405.14.6 for load categories indicated in Table C405.14.2 and Sections C405.14.7 through C405.14.11 for end-use categories indicated in Table C405.14.8.

Exceptions:

1.	Dwelling units in R-2 occupancies.

2. Individual tenant spaces are not required to comply with this section provided that the space has its own utility services and meters and has less than 5,000 square feet (464.5 m2) of conditioned floor area.

C405.14.1 Electrical energy metering.

and its associated site, including but not limited to site lighting, parking, recreational facilities and other areas that serve the building and its occupants, meters or other measurement devices shall be provided to collect energy consumption data for each end-use category required by Section C405.14.2.

C405.14.2 End-use electric metering categories.

Meters or other approved measurement devices shall be provided to collect energy use data for each end-use category indicated in Table C405.14.2. Where multiple meters are used to measure any end-use category, the data acquisition system shall total all of the energy used by that category. Not more than 5 percent of the design load for each of the end-use categories indicated in Table C405.14.2 shall be permitted to be from a load that is not within that category.

Exceptions:

1.	HVAC and water heating equipment serving only an individual dwelling unit shall not require end-use metering.

2.	End-use metering shall not be required for fire pumps, stairwell pressurization fans or any system that operates only during testing or emergency.

3.	End-use metering shall not be required for an individual tenant space having a floor area not greater than 2,500 square feet (232 m2) where a dedicated source meter complying with Section C405.14.3 is provided.

TABLE C405.14.2

ELECTRICAL ENERGY USE CATEGORIES

| LOAD CATEGORY | DESCRIPTION OF ENERGY USE |
| --- | --- |
| Total HVAC system | Heating, cooling and ventilation, including but not limited to fans, pumps, boilers, chillers and water heating. Energy used by 120-volt equipment, or by 208/120-volt equipment that is located in a building where the main service is 480/277-volt power, is permitted to be excluded from total HVAC system energy use. |
| Interior lighting | Lighting systems located within the building. |
| Exterior lighting | Lighting systems located on the building site but not within the building. |
| Plug loads | Devices, appliances and equipment connected to convenience receptacle outlets. |
| Process load | Any single load that is not included in an HVAC, lighting or plug load category and that exceeds 5 percent of the peak connected load of the whole building, including but not limited to data centers, manufacturing equipment and commercial kitchens. |
| Building operations and other miscellaneous loads | The remaining loads not included elsewhere in this table, including but not limited to vertical transportation systems, automatic doors, motorized shading systems, ornamental fountains, fireplaces, swimming pools, spas and snow-melt systems. |
| Electric hot water heating for uses other than space conditioning | Electricity used to generate hot water. Exception: Electric water heating with design capacity that is less than 10 percent of the building service rating. |
| Electric vehicle charging | Electric vehicle charging loads that are powered through the building's electrical service. |

C405.14.3 Electrical Meters.

Meters or other measurement devices required by this section shall be configured to automatically communicate energy consumption data to the data acquisition system required by Section C405.14.4. Source meters shall be allowed to be any digital-type meter. Lighting, HVAC or other building systems that can self-monitor their energy consumption shall be permitted instead of meters. Current sensors shall be permitted, provided that they have a tested accuracy of ±2 percent. Required metering systems and equipment shall have the capability to provide at least hourly data that is fully integrated into the data acquisition system and graphical energy report in accordance with Sections C405.14.4 and C405.14.5. Nonintrusive load monitoring (NILM) packages that extract energy consumption data from detailed electric waveform analysis shall be permitted to substitute for individual meters if the equivalent data is available for collection in Section C405.14.4 and reporting in Section C405.14.5.

C405.14.4 Electrical energy data acquisition system.

A data acquisition system shall have the capability to store the data from the required meters and other sensing devices for a minimum of 36 months. The data acquisition system shall have the capability to store real-time energy consumption data and provide hourly, daily, monthly and yearly logged data for each end-use category required by Section C405.14.2. The data acquisition system

shall have the capability of providing building total peak electric demand and the time(s) of day and time(s) per month at which the peak occurs. Peak demand shall be integrated over the same time period as the underlying whole-building meter reading rate.

C405.14.5 Graphical energy report.

A permanent and readily available reporting mechanism shall be provided in the building for access by building operation and management personnel. The reporting mechanism shall have the capability to graphically provide the energy consumption for each end-use category required by Section C405.14.2 not less than every hour, day, month and year for the previous 36 months.

C405.14.6 Renewable energy.

On-site renewable energy sources shall be metered with no less frequency than nonrenewable energy systems in accordance with Section 405.14.3.

C405.14.7 Nonelectrical energy submetering.

For all nonelectrical energy supplied to the building and its associated site that serves the building and its occupants, submeters or other measurement devices shall be provided to collect energy consumption data for each end-use category required by Section C405.14.8.

Exceptions:

1. HVAC and water heating equipment serving only an individual dwelling unit shall not require end-use submetering.

2. End-use submetering shall not be required for fire pumps, stairwell pressurization fans or any system that operates only during testing or emergency.

3. End-use submetering shall not be required for an individual tenant space having a floor area not greater than 2,500 square feet (232 m2) where a dedicated source meter complying with Section C405.14.9 is provided.

4. Equipment powered primarily by solid fuels serving loads other than building heating and service water heating loads.

C405.14.8 End-use nonelectrical submetering categories.

Submeters or other approved measurement devices shall be provided to collect energy use data for each end-use category indicated in Table C405.14.8. Where multiple submeters are used to measure any end-use category, the data acquisition system shall total all of the energy used by that category. Not more than 5 percent of the design load for each of the end-use categories indicated in Table C405.14.8 shall be permitted to be from a load that is not within that category.

TABLE C405.14.8

NONELECTRICAL ENERGY USE CATEGORIES

| END USE CATEGORY | DESCRIPTION OF END USE |
| --- | --- |
| Total HVAC system | Heating and cooling systems, including but not limited to boilers, chillers and furnaces. District heating and cooling energy entering the building’s distribution system shall be monitored at the point of entry to the building distribution system. |
| Process loads | Any single load that is not included in the HVAC or service water heating categories where the rated fuel gas or fuel oil input of the load and that is not less than 5 percent of the sum of the rated fuel gas or fuel oil input of all monitored equipment, including but not limited to manufacturing equipment, process equipment, commercial kitchens, and commercial laundry equipment. |
| Other miscellaneous loads | The remaining loads not included elsewhere in this table, including but not limited to fireplaces, swimming pools, spas, gas lighting, and snow-melt systems. |
| Service water heating | Fuel used to heat potable water. Exception: Water heating with design capacity that is less than 10 percent of the sum of the rated fuel gas or fuel oil input of all monitored equipment. |

C405.14.9 Nonelectrical submeters.

Submeters or other measurement devices required by this section shall be configured to automatically communicate energy consumption data to the data acquisition system required by Section C405.14.10. Source submeters shall be allowed to be any digital-type meter that can provide a digital output to the data acquisition system. Required submetering systems and equipment shall be fully integrated into the data acquisition system and graphical energy report that updates at least hourly in accordance with Sections C405.14.10 and C405.14.11.

C405.14.10 Nonelectrical energy data acquisition system.

A data acquisition system shall have the capability to store the data from the required submeters and other sensing devices for not less than 36 months. The data acquisition system shall have the capability to store real-time energy consumption data and provide hourly, daily, monthly and yearly logged data for each end-use category required by Section C405.14.8. The data acquisition system shall have the capability of providing building total nonelectrical peak demand and the time(s) of day and time(s) per month at which the peak occurs. Where applicable as determined by the authority having jurisdiction (AHJ), peak demand shall be integrated over the same time period as the underlying whole-building meter reading rate.

C405.14.11 Graphical energy report.

A permanent and readily accessible reporting mechanism shall be provided in the building that is accessible by building operation and management personnel. The reporting mechanism shall have the capability to graphically provide the nonelectrical energy consumption for each end-use category required by Section C405.14.8 not less than every hour, day, month and year for the previous 36 months. The graphical report shall incorporate natural gas interval data from the submeter or the ability to enter gas utility bills into the report.

Section C405.17 Electrification Ready.

Section C405.17 – Delete Section C405.17 in its entirety.

SECTION C406

ADDITIONAL EFFICIENCY, RENEWABLE AND LOAD MANAGEMENT REQUIREMENTS

Section C406.1.1.2 Building core/shell and build-out construction

Section C406.1.1.2- Delete item 3.3

Section C406.2.1.6 E06 Improve fenestration.

Section C406.2.1.6- Revise section C406.2.1.6 to read as follows:

C406.2.1.6 6 E06 Improve fenestration. Reserved

Section C406.2.3.1.3 W03 Efficient fossil fuel water heater.

Section C406.2.3.1.3 - Revise section C406.2.3.1.3 to read as follows:

C406.2.3.1.3 W03 Efficient fossil fuel water heater. Reserved

Section C406.2.3.1.4 Combination service water heating systems.

Section C406.2.3.1.4 - Revise section C406.2.3.1.3 to read as follows:

C406.2.3.1.4 Combination service water heating systems. Where service water heating employs both energy recovery and heat pump water heating, W01 may be combined with W02 and receive the sum of both credits.

Section C406.2.6.1 Q01 Efficient elevator equipment.

Section C406.2.6.1 - Revise section C406.2.6.1 to read as follows:

C406.2.6.1 Q01 Efficient elevator equipment. Reserved

Section C406.2.6.2 Q02 Efficient commercial kitchen equipment.

Section C406.2.6.2 - Revise section C406.2.6.2 to read as follows:

C406.2.6.2 Q02 Efficient commercial kitchen equipment. Reserved

Table C406.2.6.2(1) Minimum Efficiency Requirements: Commercial Fryers.

Table C406.2.6.2(1) – Delete Table C406.2.6.2(1) in its entirety.

Table C406.2.6.2(2) Minimum Efficiency Requirements: Commercial Steam Cookers.

Table C406.2.6.2(2) – Delete Table C406.2.6.2(2) in its entirety.

Table C406.2.6.2(3) Minimum Efficiency Requirements: Commercial Dishwashers.

Table C406.2.6.2(3) – Delete Table C406.2.6.2(3) in its entirety.

Table C406.2.6.2(4) Minimum Efficiency Requirements: Commercial Ovens.

Table C406.2.6.2(4) – Delete Table C406.2.6.2(4) in its entirety.

SECTION C407

SIMULATED BUILDING PERFORMANCE

Section C407 Simulated Building Performance.

Section C407 – Delete Section C407 in its entirety and add Section C407 to read as follows:

SECTION C407

RESERVED

SECTION C408

MAINTENANCE INFORMATION AND SYSTEM COMMISSIONING

Section C408.2 Mechanical systems, renewable energy, and service water-heating systems commissioning and completion requirements.

Section C408.2 – Revise Section C408.2 to read as follows:

C408.2 Mechanical systems, renewable energy, and service water-heating systems commissioning and completion requirements.

Prior to the final mechanical and plumbing inspections, the approved agency shall provide evidence of mechanical systems commissioning and completion in accordance with the provisions of this section.

Construction document notes shall clearly indicate provisions for commissioning and completion requirements in accordance with this section and are permitted to refer to specifications for further requirements. Copies of all documentation shall be given to the owner or owner’s authorized agent and made available to the building official upon request in accordance with Sections C408.2.4 and C408.2.5.

Mechanical systems, renewable energy, and service water heating systems shall include but are not limited to, at a minimum, the following heating, ventilating, air conditioning, service water heating, indoor air quality and refrigeration systems (mechanical and/or passive) and associated controls:

1.	Heating, cooling, air handling and distribution, ventilation, and exhaust systems, and their related air quality monitoring systems.

2.	Air, water, and other energy recovery systems.

3.	Manual or automatic controls, whether local or remote, on energy using systems including but not limited to temperature controls, setback sequences, and occupancy-based control, including energy management functions of the building management system.

4.	Plumbing, including insulation of piping and associated valves, domestic and process water pumping, and mixing systems.

5.	Mechanical heating systems and service water heating systems.

6.	Refrigeration systems.

7.	Renewable energy and energy storage systems.

8.	Other systems, equipment and components that are used for heating, cooling or ventilation and that affect energy use.

Exceptions: The following systems are exempt:

1.	 Buildings with less than 10,000 square feet (929 m2) gross conditioned floor area and combined heating, cooling and service water heating capacity of less than 960,000 Btu/h (281 kW).

2.   Components within dwelling units and sleeping units served by one of the following systems:

2.1. Simple unitary or packaged HVAC equipment listed in Table C403.3.2(1), C403.3.2(2), C403.3.2(4) or C403.3.2(5), each serving one zone and controlled by a single thermostat in the zone served.

2.2. Two-pipe heating systems installed in the dwelling, serving one or more zones .

3. 	Renewable energy systems being installed with a generating capacity of less than 25 kW.

Section C408.2.1 Commissioning plan.

Section C408.2.1 – Revise Item 2 from  Section C408.2.1 to read as follows:

2.	A listing of the specific equipment, appliances or systems to be tested their full sequences of operation, and a description of the tests to be performed, including prerequisite activities and reference to specific checklists or worksheets which are necessary or required by the department.

Section C408.2.2 Systems adjusting and balancing.

Section C408.2.2 – Revise Section C408.2.2 to read as follows:

C408.2.2 Systems adjusting and balancing.  HVAC systems shall be balanced in accordance with ASHRAE 111, “Testing, Adjusting, and Balancing of Building HVAC Systems” or other accepted engineering standards. Air and water flow rates shall be measured and adjusted to deliver final flow rates within the tolerances provided in the product specifications. Test and balance activities shall include air system and hydronic system balancing.

Section C408.2.2.1 Air systems balancing.

Section C408.2.2.1 – Delete exception from Section C408.2.2.1.

Section C408.2.3.1 Air systems balancing.

Section C408.2.2.1 – Revise  exception from Section C408.2.3.1 to read as follows:

Exception: Unitary or packaged HVAC equipment listed in the tables in Section C403.3.2 that do not require supply air economizers shall only be required to demonstrate functioning under full-load and part-load conditions.

Section C408.2.4 Preliminary commissioning report.

Section C408.2.4 – Revise  the first sentence  from Section C408.2.4 to read as follows:

A preliminary report of commissioning test procedures and results shall be completed and certified by the approved agency and provided to the building owner or owner’s authorized agent.

Section C408.2.4.1 Acceptance of report.

Section C408.2.4.1 – Revise  Section C408.2.4 to read as follows:

C408.2.4.1 Acceptance of report.  Buildings, or portions thereof, shall not be considered as acceptable for a final inspection pursuant to Chapter 1 of this code until the building official has received a letter of transmittal from the building owner acknowledging that the building owner or owner’s authorized agent has received the Preliminary Commissioning Report.

Section C408.2.5 Documentation requirements.

Section C408.2.5 – Delete Section C408.2.5, Section C408.2.5.1 and Section C408.2.5.2 and add new  Section C408.2.5, Section C408.2.5.1, Section C408.2.5.2, Section C408.2.5.3, Section C408.2.5.4 to read as follows:

C408.2.5 Documentation requirements.  The construction documents shall specify that the documents described in Sections C408.2.5.1 through C408.2.5.3  be provided to the building owner or owner’s authorized agent within 90 days of the date of receipt of the certificate of occupancy or letter of completion. The construction documents shall also specify that the Final Commissioning Report be provided to the building owner or owner’s authorized agent in accordance with the requirements of Section C408.2.5.4

C408.2.5.1 Drawings.  Construction documents shall include the location and performance data on each piece of equipment.

C408.2.5.2 Manuals.  An operating and maintenance manual shall be provided and include all of the following:

1.	Submittal data stating equipment size and selected options for each piece of equipment requiring maintenance.

2.	Manufacturer’s operation manuals and maintenance manuals for each piece of equipment requiring maintenance, except equipment not furnished as part of the project. Required routine maintenance actions shall be clearly identified.

3.	Name and address of at least one service agency.

4.	HVAC and service hot water controls system maintenance and calibration information, including wiring diagrams, schematics and control sequence descriptions. Desired or field-determined set points shall be permanently recorded on control drawings at control devices or, for digital control systems, in system programming instructions.

5.	Submittal data indicating all selected options for each piece of lighting equipment and lighting controls.

6.	Operation and maintenance manuals for each piece of lighting equipment. Required routine maintenance actions, cleaning and recommended relamping shall be clearly identified.

7.	A schedule for inspecting and recalibrating all lighting controls.

8.	A narrative of how each system is intended to operate, including recommended set points.

C408.2.5.3 System balancing report. A written report describing the activities and measurements completed in accordance with Section C408.2.2.

C408.2.5.4 Final commissioning report. Within 30 months for new buildings 500,000 gross square feet (46 452 m²) or greater, excluding R-2 occupancies, or within 18 months for R-2 occupancies and all other buildings, of the issuance of the certificate of occupancy or letter of completion, an approved agency shall prepare a report of test procedures and results, including test procedures and results performed after occupancy, identified as the "Final Commissioning Report,” provide such report to the building owner, and submit a certification to the department with applicable fees in accordance with department rules. The owner of a building 500,000 gross square feet (46 452 m²) or greater may apply for an extension of time to the building official based on good cause, in accordance with department rules. Such report shall include the following:

1.	Results of functional performance tests.

2.	Disposition of deficiencies found during testing, including details of corrective measures used or proposed.

3.	Functional performance test procedures used during the commissioning process including measurable criteria for test acceptance, provided herein for repeatability.

Exception: Deferred tests that cannot be performed at the time of report preparation due to climatic conditions.

Section C408.3.1 Functional testing.

Section C408.3.1 – Revise the first sentence of Section C408.3.1 to read as follows:

Prior to passing final inspection, the approved agency shall provide evidence that the lighting and receptable control systems have been tested to ensure that control hardware and software are calibrated, adjusted, programmed and in proper working condition in accordance with the construction documents and manufacturer’s instructions.

Section C408.4 Air barrier commissioning.  .

Section C408.4 – Add new Section C408.4, Section C408.4.1, Section C408.4.2, Section C408.4.3   to read as follows:

C408.4 Air barrier commissioning.  For new buildings or additions that are 10,000 gross square feet (929 m2) and greater, prior to passing final inspection, the approved agency shall provide evidence of air barrier commissioning and substantial completion in accordance with the provisions of Sections C408.4.1 through C408.4.3.

C408.4.1 Documentation.  Construction documents shall include documentation of the continuous air barrier components included in the design and a field inspection checklist that includes all requirements necessary for maintaining air barrier continuity and durability in accordance with Section C402.6.

C408.4.2 Field inspections.  Reports from field inspections during project construction showing compliance with continuous air barrier requirements including proper material handling and storage, use of approved materials and material substitutes, proper material and surface preparation, and air barrier continuity shall be provided to the owner and, upon request, to the building official. Air barrier continuity shall be determined by testing or inspecting each type of unique air barrier joint or seam in the building envelope for continuity and defects.

C408.4.3 Report.  A Final Commissioning Report indicating compliance with the continuous air barrier requirements shall be provided to the building owner and, upon request, to the building official.

CHAPTER C5

EXISTING BUILDINGS

SECTION ECC C501

GENERAL

Section C501.1 Scope.

Section C501.1 – Revise Section C501.1 to read as follows:

C501.1 Scope.  The provisions of this chapter shall control the alteration, repair, addition and change of occupancy of existing buildings and structures. This chapter shall not apply to alterations required to comply with new building provisions as determined by 28-101.4.5 of the New York City Administrative Code.

Section C501.2 Compliance.

Section C501.2 – Revise Section C501.2 to read as follows:

C501.2 Compliance.  Additions, alterations, repairs, and changes of occupancy to, or relocation of, existing buildings and structures shall comply with Sections C502, C503, C504 and C505 of this code, as applicable, and with the provisions for alterations, repairs, additions and changes of occupancy or relocation, respectively, in the New York City Construction Codes, , New York City Fire Code, and the New York City Electrical Code.

Exception: Additions, alterations, repairs or changes of occupancy complying with 2025 NYC ASHRAE 90.1.

Section C501.6 Change in space conditioning.

Section C501.6 – Revise Section C501.6 to read as follows:

C501.6 Change in space conditioning. Any nonconditioned or low-energy building or space that is altered to become conditioned space shall be required to   comply with Section C502.

Exception: Where the component performance alternative in Section C402.1.4 is used to comply with this section, the proposed UA shall be not greater than 110 percent of the target UA.

SECTION ECC C502

ADDITIONS

Section C502.1 General.

Section C502.1 – Revise Section C502.1 to read as follows:

C502.1 General.  Additions to an existing building, building system or portion thereof shall conform to the provisions of this code as those provisions relate to new construction without requiring the unaltered portion of the existing building or building system to comply with this code. Additions shall not create an unsafe or hazardous condition or overload existing building systems. An addition shall be deemed to comply with this code if the addition alone complies or if the existing building and addition comply with this code as a single building.  Altered portions of the building filed in conjunction with an addition shall comply with section C503.

Section C502.3.1 Vertical fenestration area.

Section C502.3.1 – Revise Item 1 from Section C502.3.1 to read as follows:

1.	Where an addition has a new vertical fenestration area that results in a total building fenestration area less than or equal to that permitted by Section C402.5.1, the addition shall comply with Section C402.1.4, C402.5.3.

Section C502.3.1 – Revise Item 3 from Section C502.3.1 to read as follows:

3.	Where an addition has vertical fenestration that results in a total building vertical fenestration area exceeding that permitted by Section C402.5.1.2, the addition shall comply with Section C402.1.4.

Section C502.3.2 Skylight area.

Section C502.3.2 – Revise Item 1 from Section C502.3.2 to read as follows:

1.	Where an addition has new skylight area that results in a total building fenestration area less than or equal to that permitted by Section C402.5.1, the addition shall comply with Section C402.1.4.

Section C502.3.2 – Revise Item 3 from Section C502.3.2 to read as follows:

3.	Where an addition has skylight area that results in a total building skylight area exceeding that permitted by Section C402.5.1.2, the addition shall comply with Section C402.1.4.

Section C502.3.4 Service water-heating systems.

Section C502.3.4 – Revise Section C502.3.4 to read as follows:

C502.3.4 Service water-heating systems. New service water-heating equipment, controls and service water-heating piping shall comply with Section C404 and C408.

Section C502.3.7 Additional energy efficiency credits.

Section C502.3.7 – Delete exception 5 from Section C502.3.7.

SECTION ECC C503

ALTERATIONS

Section C503.1 General.

Section C503.1– Revise Section C503.1 to read as follows:

C503.1 General.  Alterations to any building or structure shall comply with the requirements of Section C503. Alterations shall be such that the existing building or structure is not less conforming to the provisions of this code than the existing building or structure was prior to the alteration. Alterations to an existing building, building system or portion thereof shall conform to the provisions of this code as those provisions relate to new construction without requiring the unaltered portions of the existing building or building system to comply with this code. Subsequent subsections of section C503 shall not be construed as limiting the scope of C503.1 through omission. Alterations shall not create an unsafe or hazardous condition or overload existing building systems.

Exception: The following types of work  need not comply with the requirements for new construction, provided that the energy use of the building is not increased:

1.	Storm windows installed over existing fenestration.

2.	Surface-applied window film installed on existing single-pane fenestration assemblies reducing solar heat gain, provided that the code does not require the glazing or fenestration to be replaced.

5.	Roof recover.

4. Roof replacement where roof assembly insulation is integral to or located below the structural roof deck.

6.	Roofs without insulation in the cavity and where the sheathing or insulation is exposed during reroofing shall be insulated either above or below the sheathing.

5.	Air barriers shall not be required for roof recover and roof replacement where the alterations or renovations to the building do not include alterations, renovations or repairs to the remainder of the building thermal envelope.

6. Replacement of existing doors that separate conditioned space from the exterior shall not require the installation of a vestibule or revolving door, provided, however, that an existing vestibule that separates such conditioned space from the exterior shall not be removed.

Section C503.2 Building thermal envelope.

Section C503.2 – Revise Section C503.2 to read as follows:

C503.2 Building thermal envelope. Alterations of existing building thermal envelope assemblies shall comply with this section. New building thermal envelope assemblies that are part of the alteration shall comply with Section C402. An area-weighted average U-factor for new and altered portions of the building thermal envelope shall be permitted to satisfy the U-factor requirements in Section C402.1.4. The existing R-value of insulation shall not be reduced or the U-factor of a building thermal envelope assembly be increased as part of a building thermal envelope alteration.

Exception: Where the existing building exceeds the fenestration area limitations of Section C402.5.1 prior to alteration, the building is exempt from Section C402.5.1 provided that there is no increase in fenestration area.

Section C503.2.1 Roof replacement.

Section C503.2.1 – Revise the exception from Section C503.2.1 to read as follows:

Exceptions: Where replacement of ceiling finishes exposes cavities of the roof-ceiling construction, that is part of the building thermal envelope, the cavities shall be insulated to full depth with insulation that complies with Section C303.1.4 and having a minimum nominal value of R-3.5 per inch.

Section C503.2.2 Vertical fenestration.

Section C503.2.2 – Revise Section C503.2.2 to read as follows :

C503.2.2 Vertical fenestration.  The addition of vertical fenestration that results in a total building fenestration area less than or equal to that specified in Section C402.5.1 shall comply with Section C402.1.4, C402.5.3. The addition of vertical fenestration that results in a total building fenestration area greater than Section C402.5.1 shall comply with Section C402.5.1.1 for the space adjacent to the new fenestration only. Alterations that result in a total building vertical fenestration area exceeding that specified in Section C402.5.1.1 shall comply with Section C402.1.4.

Section C503.2.3 Skylight area.

Section C503.2.3 – Revise Section C503.2.3 to read as follows:

C503.2.3 Skylight area.  New skylight area that results in a total building skylight area less than or equal to that specified in Section C402.5.1 shall comply with Section C402.1.4, C402.5. The addition of skylight area that results in a total building skylight area greater than Section C402.5.1 shall comply with Section C402.5.1.2 for the space adjacent to the new skylights. Alterations that result in a total building skylight area exceeding that specified in Section C402.5.1.2 shall comply with Section C402.1.4.

Section C503.2.4 Above-grade wall alterations.

Section C503.2.4 – Revise Item 2 from Section C503.2.4 to read as follows:

2. Where wall cavities are exposed, the cavities shall be insulated to full depth with insulation complying with Section C303.1.4 and having a minimum nominal value of R-3.5 per inch.

Section C503.3 Heating and cooling systems.

Section C503.3 – Revise Section C503.3 to read as follows:

C503.3 Heating and cooling systems.  New heating, cooling, piping and duct systems that are part of the alteration shall comply with Sections C403 and C408. Alterations to heating, cooling duct, and piping systems shall comply with Sections C403 and C408.

Section C503.3.4 Controls.

Section C503.3.4 – Revise Section C503.3.4 to read as follows:

C503.3.4 Controls. New HVACR systems that are part of the alteration shall be provided with controls that comply with Section C403.4. Altered controls shall comply with Section C403.4. Where controls are altered for more than 50% of the terminal distribution elements of a heating or cooling system, the controls for all commonly served terminal distribution elements and the associated, immediately upstream plant equipment shall comply with section C403.4 as new.

Exceptions:

1. Controls for terminal distribution elements located in a space occupied by a different tenant than the altered space.

2. Control provisions of section C403.4 which are impossible to achieve without an alteration of otherwise unaltered non-control elements of the associated, immediately upstream plant equipment.

Section C503.3.5 System sizing.

Section C503.3.3 – Revise Section C503.3.5 to read as follows:

C503.3.5 System sizing.  New heating, cooling and ventilation systems that is part of an alteration shall be sized in accordance with Section C403.1.1 based on the existing building features as modified by the alteration.

Exception:

1. Where it is demonstrated to the building official that compliance with this section would result in heating or cooling equipment that is deemed by the commissioner incompatible with the rest of the heating or cooling system.

2. Where it has been demonstrated to the building official that the additional capacity will be needed in the future.

Section C503.6 Additional energy efficiency credit requirements for alterations.

Section C503.6 – Revise exception 3 from Section C503.6 to read as follows:

3. Reserved. Section C505.1 General..

Section C505.1 – Delete the exception to Section C505.1.

Section C505.2.1 Building thermal envelope.

Section C505.2.1 – Revise Section C505.2.1 to read as follows:

C505.2.1 Building thermal envelope. Where a change of occupancy results in a fenestration area greater than the maximum fenestration area allowed by Section C402.5.1, the building shall comply with Section C402.1.4, with a proposed EPF that shall be not greater than 110 percent of the target UA.

Exception: Where the change of occupancy or use is made to a building or a portion of the building that is less than 2,000 square feet, the new occupancy is exempt from Section C402.5.1, provided that there is not an increase in fenestration area.

Table C505.2.2—Building Mechanical Systems.

Table C505.2.2– Revise Table C505.2.2 to read as follows:

TABLE C505.2.2—BUILDING MECHANICAL SYSTEMS

| ENERGY USE INTENSITY RANK | NEW YORK CITY BUILDING CODE OCCUPANCY CLASSIFICATION AND USE |
| --- | --- |
| High | A-2, B (laboratories), I-2 |
| Medium | A-1, A-3,a A-4, A-5, B,b E, I-1, I-3, I-4, M |
| Low | A-3 (places of religious worship), R-1, R-2, R-3,c S-1, S-2, F, H, U |

a. Excluding places of religious worship.

b. Excluding laboratories.

c. Buildings three stories or less in height above grade plane shall comply with Section R505.

Table C505.2.3—Service Water Heating.

Table C505.2.3– Revise Table C505.2.3 to read as follows:

TABLE C505.2.3—SERVICE WATER HEATING

| ENERGY USE INTENSITY RANK | NEW YORK CITY BUILDING CODE OCCUPANCY CLASSIFICATION AND USE |
| --- | --- |
| High | A-2, I-1, I-2, R-1 |
| Low | All other occupancies and uses |

Table C505.2.4—Lighting.

Table C505.2.4– Revise Table C505.2.4 to read as follows:

TABLE C505.2.4—LIGHTING

| ENERGY USE INTENSITY RANK | NEW YORK CITY BUILDING CODE OCCUPANCY CLASSIFICATION AND USE |
| --- | --- |
| High | B (laboratories), B (outpatient healthcare), I-2, M |
| Medium | A-2, A-3 (courtrooms), B,a I-1, I-3, I-4, R-1, R-2, R-3,b R-4, S-1, S-2 |
| Low | A-1, A-3,c A-4, E |

a. Excluding laboratories and outpatient healthcare.

b. Buildings three stories or less in height above grade plane shall comply with Section R505.

c. Excluding courtrooms.

CHAPTER C6

CHAPTER R2

DEFINITIONS

SECTION R201

GENERAL

Section R201.1 Scope.

Section R201.1 - Revise Section R201.1 to read as follows:

R201.1 Scope. Unless stated otherwise, the words and terms provided in italics within this code shall have the meanings as defined in Section R202, C202 or as defined within the chapter or appendix where the word or term is found, except as provided in Sections R201.3 and R201.4.

Section R201.3 Terms defined in other codes.

Section R201.3 - Revise Section R201.3 to read as follows:

R201.3 Terms defined in other codes. Where italicized words and terms are not defined in this code but are defined in the New York City Construction Codes, New York City Fire Code, or the New York City Electrical Code shall have the meanings ascribed to them in those codes.

Section R202

GENERAL DEFINITIONS

Section R202 - Delete the definitions of “Building Code of New York State,” “Existing Building Code of New York State,” “Fire Code of New York State,” “Fuel Gas Code of New York State,” “Mechanical Code of New York State,” “Plumbing Code of New York State,” ”Property Maintenance Code of New York State,” “Residential Code of New York State,” and “Uniform Code.”

Section R202 – Add the definitions of  “2025 NYC ASHRAE 90.1” after the definition of “2025 NYS ASHRAE 90.1.” to read as follows:

2025 NYC ASHRAE 90.1. New York City amendments to 2025 NYS ASHRAE 90.1

Section R202 - Delete the definitions of “Approved,” “Approved agency,” after the definition of “Alteration.”

Section R202 – Add the definitions of “Approved,” “Approved agency,” after the definition of “Alteration,” to read as follows:

APPROVED. See Section 28-101.5 of the Administrative Code.

APPROVED AGENCY. See Section 28-101.5 of the Administrative Code.

Section R202 – Delete the definitions of “Area-weighted average,” “Authority having jurisdiction,”  after the definition of “Approved source.”

Section R202 – Add the definitions of “Area-weighted average,”  “Authority having jurisdiction,” after the definition of “Approved source.” to read as follows:

AREA WEIGHTED AVERAGE. A mathematical technique for combining different amounts of various components, based on proportional relevance, into a single number. Weighted averaging may be used where there is more than one insulation or thermal resistance value for floor, wall, ceiling insulation, for fenestration in a building. As an example, the area weighted average for window fenestration U-factors equals (Area 1 × U-factor 1) + (Area 2 × U-factor 2) + …/Total Area = weighted average fenestration U-factor.

AUTHORITY HAVING JURISDICTION. The governmental unit or agency responsible for administration and enforcement of the New York City Building Codes and NYCECC.

Section R202 – Delete the definitions of “Basement wall,” after the definition of “Balanced ventilation system.”

Section R202 – Add the definitions of “Basement or cellar, Energy Code,” “Basement wall,”  “Below-grade wall,” after the definition of “Balanced ventilation system.” to read as follows:

BASEMENT OR CELLAR, ENERGY CODE. A story that is not a story above grade plane. See the definition of “Story above grade plane.”

BASEMENT WALL. See “Below-grade wall”

BELOW-GRADE WALL. A wall where 50 percent or more of the total surface area is below the adjoining grade and enclosing conditioned space.

Section R202 – Delete the definitions of “Building official,” after the definition of “Building.”

Section R202 – Add the definitions of “Building official” after the definition of “Building.” to read as follows:

BUILDING OFFICIAL. The Commissioner of Buildings of the City of New York or his or her duly authorized representative. See Section 28-101.5 of the Administrative Code.

Section R202 – Delete the definitions of “Building Thermal Envelope,” after the definition of “Building System.”

Section R202 – Add the definitions of “Building Thermal Envelope” after the definition of “Building System.to read as follows:

BUILDING THERMAL ENVELOPE. The exterior walls, floors, ceilings, slabs, roofs,  fenestration and any other building element assemblies (above and below grade) that enclose conditioned space or provide a boundary between conditioned space and exempt or unconditioned space.

Section R202 – Add the definitions of “Commissioner” after the definition of “Commercial building.” to read as follows:

COMMISSIONER. The commissioner of buildings of the city of New York, or his or her duly authorized representative.(See “Authority Having Jurisdiction” and “Building official”)

Section R202 – Delete the definitions of “Enclosed Reflective Airspace,” after the definition of “Emittance.”

Section R202 – Add the definitions of “Embodied Carbon, ” “Enclosed Reflective Airspace.” after the definition of “Emittance.” to read as follows:

EMBODIED CARBON: The total greenhouse gas emissions associated with the life cycle of building materials and products, excluding operational emissions from the building itself.

ENCLOSED REFLECTIVE AIRSPACE. An unventilated cavity with at least one low-emittance surface adjacent to an empty air space bounded on all sides by building components.

Section R202 – Delete the definitions of “Energy code,” “Energy cost,”  after the definition of “Energy analysis.”

Section R202 – Add the definitions of “Energy code, after the definition of “Energy analysis.” to read as follows:

ENERGY CODE. The New York City Energy Conservation Code.

Section R202 – Delete the definitions of “Grade Plane,”   after the definition of “Fuel oil.”

Section R202 – Add the definitions of “Grade Plane, Energy,” after the definition of “Fuel Oil.” to read as follows:

GRADE PLANE, ENERGY. A reference plane representing the average of the finished ground level adjoining the building at all exterior walls. Where the finished ground level slopes away from the exterior walls, the reference plane is established by the lowest points within the area between the building and the lot line or, where the lot line is more than 6 feet (1829 mm) from the building, between the structure and a point 6 feet (1829 mm) from the building.

Section R202 – Delete the definitions of “Market value,”   after the definition of “Manual.”

Section R202 – Add the definitions of “Professional certification,” “Project” after the definition of “Plenum.” to read as follows:

PROFESSIONAL CERTIFICATION. See Section 28-101.5 of the Administrative Code.

PROJECT. A design and construction undertaking comprised of work related to one or more buildings and the site improvements. A project is represented by one or more plan/work applications, including construction documents compiled in accordance with Section 107 of the New York City Building Code, that relate either to the construction of a new building or buildings or to the demolition or alteration of an existing building or buildings. Applications for a project may have different registered design professionals and different job numbers, and may result in the issuance of one or more permits.

Section R202 – Delete the definitions of “Solar Heat Gain Coefficient (SHGC)”   after the definition of “Sleeping unit.”

Section R202 – Add the definitions of “Solar Heat Gain Coefficient (SHGC),” after the definition of “Sleeping unit.” to read as follows:

SOLAR HEAT GAIN COEFFICIENT (SHGC). The ratio of the solar heat gain entering the space through the fenestration assembly to the incident solar radiation. Solar heat gain includes directly transmitted solar heat and absorbed solar radiation that is then re-radiated, conducted or transferred by convection into the space.

Section R202 – Add the definitions of “Story,” “Story above grade plane,” “Substantial Energy Alteration, “ “Substantially complete building permit application. ” after the definition of “Steep slope.” to read as follows:

STORY. The portion of a building included between the upper surface of a floor and the upper surface of the floor or roof next above. See the definitions of “Basement or Cellar, Energy Code and “Grade plane, Energy Code.” A story is measured as the vertical distance from top to top of two successive tiers of beams or finished floor surfaces and, for the topmost story, from the top of the floor finish to the top of the ceiling joists or, where there is not a ceiling, to the top of the roof rafters.

STORY ABOVE GRADE PLANE. Any story having its finished floor surface entirely above grade plane, or in which the finished surface of the floor next above is:

1.	More than 6 feet (1829 mm) above average grade plane; or

2.	More than 12 feet (3658 mm) above the finished ground level at any point.

Section R202 – Add the definitions of “Thermal Bridges” after the definition of “Testing unit enclosure area.” to read as follows:

THERMAL BRIDGES. A structural element or interface of elements that has higher thermal conductivity than the surrounding building thermal envelope, which creates a path of decreased resistance for heat transfer.

CLEAR FIELD THERMAL BRIDGE. Elements of a building envelope assembly creating paths of decreased resistance for heat transfer which repeat at regular intervals, such as metal or wood studs, girts, and purlins.

CHI-FACTOR (χ-FACTOR). The heat loss factor for a single thermal bridge characterized as a point element of a building thermal envelope (Btu/h x °F) [W/K].

Linear thermal bridge: a length-based element associated with horizontal, vertical, or diagonal elements that penetrates the insulation in the building thermal envelope and with a length measured along an exterior surface of the building thermal envelope, such as balconies, parapet-, roof-, floor-, or fenestration intersections, and shelf angles.

POINT THERMAL BRIDGE. An element that penetrates the insulation in the building thermal envelope, such as columns or beams passing through envelope assemblies, attachments, anchors, and connections not defined as clear field- or linear thermal bridges. The cross-sectional area is measured at the external surface of the outermost penetrated insulation layer.

PSI-FACTOR (ψ-FACTOR). The heat loss factor per unit length of a thermal bridge characterized as a linear element of a building thermal envelope (Btu/h x ft x °F) [W/(m x K)].

CHAPTER R3

GENERAL REQUIREMENTS

SECTION ECC R301

CLIMATE ZONES

Section R301.1 General.

Section R301.1 - Revise Section R301.1 to read as follows:

R301.1 General. For projects in the City of New York, Climate Zone 4A shall be used in determining the applicable requirements from Chapter R4.

SECTION R303

MATERIALS, SYSTEMS AND EQUIPMENT

Section R303.1.1 Building thermal envelope insulation.

Section R303.1.1 – Revise the Exception to Section R303.1.1 to read as follows:

Exception: For roof insulation installed above the deck, the R-value shall be labeled as required by the material standards specified in New York City Building Code.

Section R303.1.2 Insulation mark installation.

Section R303.1.2 – Revise the Exception to Section R303.1.2 to read as follows:

Exception: For roof insulation installed above the deck, the R-value shall be labeled as specified by the material standards in the New York City Building Code

Section R303.1.3 Fenestration product rating.

Section R303.1.3 - Revise Section R303.1.3 to read as follows:

R303.1.3 Fenestration product rating. U-factors of fenestration products such as windows, doors and skylights shall be determined in accordance with NFRC 100.

Exception: Where required, garage door U-factors shall be determined in accordance with either NFRC 100 or ANSI/DASMA 105.

U-factors shall be determined by a third-party accredited, independent laboratory, recognized by ANSI, ILAC or MiRa and labeled and certified by the manufacturer.

Products lacking such a labeled U-factor shall be assigned a default U-factor from Table R303.1.3(1) or Table R303.1.3(2). The solar heat gain coefficient (SHGC) and visible transmittance (VT) of glazed fenestration products such as windows, glazed doors and skylights shall be determined in accordance with NFRC 200 an accredited, independent laboratory, and labeled and certified by the manufacturer. Products lacking such a labeled SHGC or VT shall be assigned a default SHGC or VT from Table R303.1.3(3).

Section R303.1.6 Airspaces.

Section R303.1.6 - Revise Section R303.1.6 to read as follows:

R303.1.6 Airspaces. Where the R-value of an enclosed reflective airspace or enclosed nonreflective airspace is used for compliance with this code, the airspace shall be enclosed in a cavity bounded on all sides by building components and constructed to minimize airflow into and out of the enclosed airspace. Airflow shall be deemed minimized where one of the following conditions occur:

1.  The enclosed airspace is unventilated.

2. The enclosed airspace is bounded on one or more sides by an anchored masonry veneer, constructed in accordance with the New York City Building Code, and vented by veneer weep holes located only at the bottom portion of the airspace and spaced not less than 15 inches (381 mm) on center with the top of the cavity airspace closed.

Exception: For ventilated cavities, the effect of the ventilation of airspaces located on the exterior side of the continuous air barrier and adjacent to and behind the exterior wall covering material shall be determined in accordance with ASTM C1363, modified with an airflow entering the bottom and exiting the top of the airspace at an air movement rate of not less than 70 millimeters per second.

Section R303.2 Installation.

Section R303.2- Revise Section R303.2 to read as follows:

R303.2 Installation.   Materials, systems and equipment shall be installed in accordance with the manufacturer’s instructions and the provisions of the New York City Construction Codes.

CHAPTER R4

RESIDENTIAL ENERGY EFFICIENCY

SECTION R401

GENERAL

Section R401.3 Certificate.

Section R401.3 - Revise Section R401.3 to read as follows:

R401.3 Certificate.   A permanent certificate shall be completed by the builder or other approved party and posted on a wall in the space where the furnace is located, a utility room or an approved location inside the building. Where located on an electrical panel, the certificate shall not cover or obstruct the visibility of the circuit directory label, service disconnect label or other required labels. The certificate shall indicate the following:

1. The predominant R-values of insulation installed in or on ceilings, roofs, walls, foundation components such as slabs, below-grade walls, crawl space walls and floors and ducts outside conditioned spaces.

2.	U-factors of fenestration and the solar heat gain coefficient (SHGC) of fenestration. Where there is more than one value for any component of the building thermal envelope, the certificate shall indicate both the value covering the largest area and the area weighted average value if available.

3.	The results from any required duct system and building thermal envelope air leakage testing performed on the building.

4.	The types, sizes and efficiencies of heating, cooling and service water-heating equipment. Where a gas-fired unvented room heater, electric furnace or baseboard electric heater is installed in the residence, the certificate shall indicate “gas-fired unvented room heater,” “electric furnace” or “baseboard electric heater,” as appropriate. An efficiency shall not be indicated for gas-fired unvented room heaters, electric furnaces and electric baseboard heaters.

5.	Where on-site photovoltaic panel systems have been installed, the array capacity, inverter efficiency, panel tilt and orientation shall be noted on the certificate.

6.	For buildings where an Energy Rating Index score is determined in accordance with Section R406, the Energy Rating Index score, both with and without any on-site generation, shall be listed on the certificate.

7.	The code edition under which the structure was permitted, and the compliance path used and, where applicable, the additional efficiency measures selected for compliance with Section R408.

8. The location and dimensions of a solar-ready zone where one is provided.

SECTION R402

BUILDING THERMAL ENVELOPE

Section R402.1 General.

Section R402.1 - Revise Section R402.1 to read as follows:

R402.1 General.   The building thermal envelope shall comply with the requirements of one of the following:

1. Sections R402.1.1 through R402.1.4 and Section R402.1.6, and R402.2 through R402.7.

2. Sections R402.1.1, R402.1.5 and R402.1.6, and R402.2 through R402.7.

Section R402.1.1 General.

Section R402.1.1 - Revise Section R402.1.1 to read as follows:

R402.1.1 Vapor retarder.   Wall assemblies in the building thermal envelope shall comply with the vapor retarder requirements of the New York City Building Code, as applicable.

Table R402.1.2 Insulation and Fenestration Requirements by Componenta

Revise Table R402.1.2 to read as follows:

TABLE R402.1.2

MAXIMUM ASSEMBLY U-FACTORS AND FENESTRATION REQUIREMENTSa

| Climate Zone | 4 | 5 | 6 |
| --- | --- | --- | --- |
| Vertical Fenestration U-factor | 0.27 | 0.27c | 0.27c |
| Skylight U-factor | 0.50 | 0.50 | 0.50 |
| Glazed Vertical Fenestration SHGCc,d,f | 0.40 | NR | NR |
| Skylight SHGCd | 0.40 | NR | NR |
| Ceiling U-factor | 0.026 | 0.026 | 0.026 |
| Insulation Entirely Above Roof Deck | 0.032 | 0.032 | 0.032 |
| Wood Frame Wall U-factor | 0.045 | 0.045 | 0.045 |
| Mass Wall U-factorb | 0.060 | 0.060 | 0.060 |
| Floor U-factor | 0.033 | 0.033 | 0.033 |
| Below-grade Wall U-factor | 0.050 | 0.050 | 0.050 |
| Unheated Slab F-Factord | 0.48 | 0.48 | 0.48 |
| Heated Slab F-Factord | 0.55 | 0.55 | 0.55 |
| Crawl Space Wall U-factor | 0.055 | 0.055 | 0.055 |

For SI: 1 foot = 304.8 mm.

a.	Nonfenestration U-factors and F-factors shall be obtained from measurement, calculation, an approved source, or Appendix RF where such appendix is adopted or approved.

b.	Mass walls shall be in accordance with Section R402.2.6. Where more than half the insulation is on the interior, the mass wall U-factor shall not exceed 0.56.

c.	Reserved

d. F-factors for slabs shall correspond to the R-values of Table R402.1.3 and the installation conditions of Section R402.2.10.1.

Table R402.1.3 Insulation and Fenestration Requirements by Componenta

Revise Table R402.1.3 to read as follows:

TABLE R402.1.3

INSULATION MINIMUM R-VALUES AND FENESTRATION REQUIREMENTS BY COMPONENTa

| Climate Zone | 4 | 5 | 6 |
| --- | --- | --- | --- |
| VERTICAL Fenestration U-factorf | 0.27 | 0.27 | 0.27 |
| Skylightb U-factor | 0.50 | 0.50 | 0.50 |
| Glazed Vertical Fenestration SHGCh | 0.40 | NR | NR |
| Skylight SHGC | 0.40 | NR | NR |
| Ceiling R-Valueg | 49 ca | 49ca | 49ca |
| Insulation entirely above roof deck | 30ci | 30ci | 30ci |
| Wood Frame Wall R-Valued | 30ca or 20ca +5ci or 13ca+10ci 20ci | 30ca or 20ca+5ci or 13ca+10ci or 20ci | 30ca or 20ca+5ci or 13ca+10ci or 20ci |
| Mass Wall R-Valuee | 15ci/20ci | 15ci/20ci | 15ci/20ci |
| Floor R-Valueg | 30ca or 19ca+7.5ci or 20ci | 30ca or 19ca+7.5ci or 20ci | 30ca or 19ca+7.5ci or 20ci |
| BELOW-GRADE Wall R-Value b | 15ci or 19ca or 13ca +5ci | 15ci or 19ca or 13ca +5ci | 15ci or 19ca or 13ca +5ci |
| Unheated slab R-value & depthc | 10ci, 4 ft. | 10ci, 4 ft. | 10ci, 4 ft. |
| Heated slab R-value & depthc | 10ci 4 ft and R-10 full slab | 10ci, 4ft and R-10 full slab | 10ci, 4ft and R-10 full slab |
| Crawl Space Wall R-value b | 15ci or 19ca or 13ca +5ci | 15ci or 19ca or 13ca +5ci | 15ci or 19ca or 13ca +5ci |

- R-values are minimums. U-factors and SHGC are maximums. Where insulation is installed in a cavity that is less than the label or design thickness of the insulation, the installed R-value of the insulation shall be not less than the R-value specified in the table.

- “15ci or 19ca” means R-15 continuous insulation (ci) on the interior or exterior surface of the wall or R-19 cavity insulation on the interior side of the wall. 13ca+5ci means R-13 cavity insulation on the interior of the basement wall plus R-5 continuous insulation on the interior or exterior of the home.

- Slab insulation shall be installed in accordance with Section R402.2.9.1.

- The first value is cavity insulation, the second value is continuous insulation. Therefore, as an example, “13ca+10ci ” means R-13  cavity insulation plus R-10 continuous insulation.

- Mass walls shall be in accordance with Section R402.2.5. The second R-value applies where more than half of the insulation is on the interior of the mass wall.

- Reserved

- "30ca or 20ca+5ci or 20ci" means R-30  cavity insulation alone or R-20 cavity insulation with R-5 continuous insulation or R-20 continuous insulation alone

Section R402.1.6 Rooms containing fuel-burning appliances.

Section R402.1.6 - Revise Section R402.1.6 to read as follows:

R402.1.6 Rooms containing fuel-burning appliances.  In Climate Zones 3 through 8, where open combustion air ducts provide combustion air to open combustion fuel-burning appliances, the appliances and combustion air opening shall be located outside the building thermal envelope or enclosed in a room that is isolated from inside the building thermal envelope. Such rooms shall be sealed and insulated in accordance with the building thermal envelope requirements of Table R402.1.3, where the walls, floors and ceilings shall meet a minimum of the below-grade wall R-value requirement. The door into the room shall be fully gasketed and any water lines and ducts in the room insulated in accordance with Section R403. The combustion air duct shall be insulated where it passes through conditioned space to an R-value of not less than R-8.

Exceptions:

1.	Direct vent appliances with both intake and exhaust pipes installed continuous to the outside.

2.	Fireplaces and stoves complying with Section R402.4.2 and the New York City Mechanical Code.

Section R402.2.7 Steel-frame ceilings, walls and floors.

Section R402.2.7 – Revise Section R402.2.7 to read as follows:

R402.2.7 Steel-frame ceilings, walls and floors.  Steel-frame ceilings, walls, and floors shall comply with the ceiling, wood frame wall and floor U-factor requirements of Table R402.1.2, R-values in table R402.1.3 may not be applied. The calculation of the U-factor for steel-framed ceilings and walls in a building thermal envelope assembly shall be determined in accordance with section RF102.3.

Section R402.2.9 Basement Walls.

Section R402.2.9  - Delete Section R402.2.9  in its entirety and add a new Section R402.2.9  to read as follows:

R402.2.9 Below-grade walls.   Below-grade walls shall be insulated in accordance with Table R402.1.3.

Exception: Below-grade walls associated with unconditioned basements or cellars where the following requirements are met:

1.	The floor overhead, including the underside stairway stringer leading to the basement or cellar, is insulated in accordance with Section R402.1.3 and applicable provisions of Sections R402.2 and R402.2.7.

2.	There are no uninsulated ductwork, domestic hot water piping, or hydronic heating surfaces exposed to the basement or cellar.

3.	There are no HVAC supply or return diffusers serving the basement or cellar.

4.	The walls surrounding the stairway and adjacent to conditioned space are insulated in accordance with Section R402.1.3 and applicable provisions of Section R402.2.

5.	The door(s) leading to the basement or cellar from conditioned spaces are insulated in accordance with Section R402.1.3 and applicable provisions of Section R402.2, and weatherstripped in accordance with Section R402.4.

6.	The building thermal envelope separating the basement or cellar from adjacent conditioned spaces complies with Section R402.4.

Section R402.2.9.1 Basement wall insulation installation.

Section R402.2.9.1  - Delete Section R402.2.9.1  in its entirety and add a new Section R402.2.9.1  to read as follows:

R402.2.9.1 Below-grade wall insulation installation. Where below-grade walls are insulated, the insulation shall be installed from the top of the below-grade wall down to 10 feet (3048 mm) below grade or to the basement or cellar floor, whichever is less, or in accordance with the proposed design or the rated design, as applicable

Section R402.2.10.1 Slab-on-grade floor insulation installation.

Section R402.2.10.1  - Delete Section R402.2.10.1  in its entirety and add a new Section R402.2.10.1  to read as follows:

R402.2.10.1 Slab-on-grade floor insulation installation.   For buildings complying with Section R401.2.1, the slab edge continuous insulation shall extend downward from the top of the slab on the outside or inside of the foundation wall. Insulation located below grade shall be extended the vertical distance provided in Table R402.1.3, but need not exceed the footing depth in accordance with chapter 18 of the New York City Building Code. Where a proposed design includes insulation extending away from the building, it shall be protected by pavement or by not less than 10 inches (254 mm) of soil. The top edge of the insulation installed between the exterior wall and the edge of the interior slab shall be permitted to be cut at a 45-degree (0.79 rad) angle away from the exterior wall. Full-slab insulation shall be continuous under the entire area of the slab-on-grade floor, except at structural column locations and service penetrations. Slab edge insulation required at the heated slab perimeter shall not be required to extend below the bottom of the heated slab and shall be continuous with the full slab insulation.

Section R402.2.11.1  Crawl space wall insulation installations.

Section R402.2.11.1  - Revise the last paragraph of  Section R402.5.1  to read as follows:

Exposed earth in crawl space foundations shall be covered with a continuous Class I vapor retarder in accordance with New York City Building Code, as applicable. Joints of the vapor retarder shall overlap by 6 inches (153 mm) and be sealed or taped. The edges of the vapor retarder shall extend not less than 6 inches (153 mm) up stem walls and shall be attached to the stem walls.

Section R402.5.1 Building thermal envelope.

Section R402.5.1  - Delete Section R402.5.1  in its entirety and add a new Section R402.5.1  to read as follows:

R402.5.1 Building thermal envelope.    The building thermal envelope shall comply with Sections R402.5.1.1 through R402.5.1.4 The sealing methods between dissimilar materials shall allow for differential expansion and contraction.

Section R402.5.1.1 Installation.

Section R402.5.1.1  - Delete Section R402.5.1.1 in its entirety and add a new Section R402.5.1.1 to read as follows:

R402.5.1.1 Installation.   The components of the building thermal envelope as indicated in Table R402.4.1.1 shall be installed in accordance with the manufacturer’s instructions and the criteria indicated in Table R402.5.1.1, as applicable to the method of construction. Where required by the building official, an approved agency shall inspect all components and verify compliance. The inspection shall include an open wall visual inspection of all components included in Table R402.5.1.1. and shall be installed so that the insulation material uniformly fills each cavity side-to-side and top-to-bottom, without gaps or voids around obstructions, and is split, installed, or fitted tightly around wiring and other penetrations in the cavity. No more than 2 percent of the total insulated area shall contain gaps or voids in the insulation or be compressed below the thickness required to attain the labeled R-value.

Table R402.5.1.1 Insulation and Fenestration Requirements by Componenta

Revise Table R402.5.1.1 to read as follows:

TABLE R402.5.1.1

AIR BARRIER, AIR SEALING AND INSULATION INSTALLATIONa

| COMPONENT | AIR BARRIER, AIR SEALING CRITERIA | INSULATION INSTALLATION CRITERIA |
| --- | --- | --- |
| General requirements | A continuous air barrier shall be installed in the building thermal envelope. Breaks or joints in the air barrier shall be sealed. | Air-permeable insulation shall not be used as a sealing material. Insulation shall be installed so that the insulation material uniformly fills each cavity side-to-side and top-to-bottom, without substantial gaps or voids around obstructions, and is split, installed, or fitted tightly around wiring and other penetrations in the cavity. Not more than 2 percent of the total insulated area shall be compressed below the thickness required to attain the labeled R-value or contain gaps or voids in the insulation. |
| Ceiling/attic | An air barrier shall be installed in any dropped ceiling or soffit to separate it from unconditioned space. Access openings, drop down stairs or knee wall doors to unconditioned attic spaces shall be sealed with gasketing materials that allow for repeated entrance over time. | The insulation in any dropped ceiling/soffit shall be aligned with the air barrier. Access hatches and doors shall be installed and insulated in accordance with Section R402.2.5. Eave baffles shall be installed in accordance with Section R402.2.4. |
| Walls | The junction of the foundation and sill plate shall be sealed. The junction of the top plate and the top of exterior walls shall be sealed. Knee walls shall be sealed. | Cavities within corners and headers of frame walls shall be insulated by completely filling the cavity with a material having a thermal resistance, R-value, of not less than R-3 per inch. Exterior building thermal envelope insulation for framed walls shall be installed in substantial contact and continuous alignment with the air barrier. |
| Knee wall | Knee walls shall have an air barrier between conditioned and unconditioned space | Insulation installed in a knee wall assembly shall be installed in accordance with Section R402.2.3. Air-permeable insulation shall be enclosed inside an air barrier assembly. |
| Windows, skylights and doors | The rough opening gap between framing and the frames of skylights, windows and doors, shall be sealed in accordance with fenestration manufacturer’s instructions. | Insulation shall not be required in the rough opening gap except as required by the fenestration manufacturer's instructions. |
| Rim joists | Rim joists shall include an air barrier.b. The junctions of the rim board to the sill plate and the rim board and the subfloor shall be air sealed. | Rim joists shall be insulated so that the insulation maintains permanent contact with the exterior rim board.ᵇ |
| Floors, including cantilevered floors and floors above garages | Floor framing members that are part of the building thermal envelope shall be air sealed to maintain a continuous air barrier. Air permeable floor cavity insulation shall be enclosed. | Floor insulation shall be installed in accordance with the requirements of Section R402.2.8. |
| Basement or cellar, crawl space and slab foundations | Exposed earth in unvented crawl spaces shall be covered with a Class I vapor retarder/air barrier in accordance with Section R402.2.11. Penetrations through concrete foundation walls and slabs shall be air sealed. Class 1 vapor retarders shall not be used as an air barrier on below-grade walls and shall be installed in accordance with the New York City Building Code | Crawl space insulation, where provided instead of floor insulation, shall be installed in accordance with Section R402.2.11. Conditioned basement or cellar foundation wall insulation shall be installed in accordance with Section R402.2.9.1. Slab-on-grade floor insulation shall be installed in accordance with Section R402.2.10. |
| Shafts, penetrations | Duct and flue shafts to exterior or unconditioned space shall be sealed. Utility penetrations of the air barrier shall be caulked, gasketed or otherwise sealed and shall allow for expansion, contraction of materials and mechanical vibration. | Insulation shall be fitted tightly around utilities passing through shafts and penetrations in the building thermal envelope to maintain required R-value |
| Narrow cavities | Narrow cavities of 1 inch or less that are not able to be insulated shall be air sealed. | Batts to be installed in narrow cavities shall be cut to fit or narrow cavities shall be filled with insulation that on installation readily conforms to the available cavity space. |
| Garage separation | Air sealing shall be provided between the garage and conditioned spaces. | Insulated portions of the garage separation assembly shall be installed in accordance with Sections R303 and R402.2.8. |
| Recessed lighting | Recessed light fixtures installed in the building thermal envelope shall be air sealed in accordance with Section R402.4.5. | Recessed light fixtures installed in the building thermal envelope shall be airtight and IC rated and shall be buried in or surrounded with insulation. |
| Plumbing, wiring or other obstructions | All holes created by wiring, plumbing or other obstructions in the air barrier assembly shall be air sealed. | Insulation shall be installed to fill the available space and surround wiring, plumbing, or other obstructions, unless the required R-value can be met by installing insulation and air barrier systems completely to the exterior side of the obstructions. |
| Showers, tubs and fireplaces adjacent to the building thermal envelope | An air barrier shall separate insulation in the building thermal envelope from the shower, tub or fireplace assemblies. | Exterior framed walls adjacent to showers, tubs and fireplaces shall be insulated. |
| Electrical, communication and other equipment boxes, housings and enclosures | Boxes, housing and enclosures that penetrate the air barrier shall be caulked, taped, gasketed or otherwise sealed to the air barrier element being penetrated. All concealed openings into the box, housing or enclosure shall be sealed. Alternatively, air-sealed boxes shall be installed in accordance with Section R402.5.5. | Boxes, housing and enclosures shall be buried in or surrounded by insulation. |
| HVAC register boots | HVAC supply and return register boots shall be sealed to the subfloor, wall covering or ceiling penetrated by the boot. | HVAC supply and return register boots located within a building thermal envelope assembly shall be buried in or surrounded by insulation. |
| Concealed sprinklers | Where required to be sealed, concealed fire sprinklers shall only be sealed in a manner that is recommended by the manufacturer. Caulking or other adhesive sealants shall not be used to fill voids between fire sprinkler cover plates and walls or ceilings. |  |
| Common walls or double walls separating attached single-family dwellings or townhouses | An interior air barrier shall be provided. Air sealing at the intersections with building thermal envelope shall be provided. Where installed in a fire resistance- rated wall assembly, air sealing materials shall comply with one of the following: 1. Be in accordance with an approved design for the fire-resistance-rated assembly. 2. Be supported by approved data that shows the assembly as installed complies with the required fire resistance rating. | Insulation materials recognized in the approved common wall or double-wall design and installed in accordance with the approved design shall be permitted to be used. |

a.	Inspection of log walls shall be in accordance with the provisions of ICC 400.

b.	Insulation full enclosure is not required in unconditioned/ventilated attic spaces and at rim joists.

Section R402.5.1.2 Air leakage testing.

Section R402.5.1.2  - Delete Section R402.5.1.2 in its entirety and add a new Section R402.5.1.2 to read as follows:

R402.5.1.2 Air leakage testing.   The building shall be tested for air leakage in accordance with Sections R402.5.1.3 and R402.5.1.4. Where required by the building official, testing shall be conducted by an approved third party. A written report of the results of the test shall be signed by the party conducting the test and provided to the building official. Testing shall be performed at any time after creation of all penetrations of the building thermal envelope have been sealed.

Exception:  For heated sunrooms and heated attached private garages and heated, detached private garages accessory to one-and-two family dwellings and townhouses not more than three stories above grade plane in height, building thermal envelope tightness and insulation installation shall be considered acceptable where the items in Table R402.5.1.1, applicable to the method of construction, are field verified. Where required by the building official, an approved third party independent from the installer shall inspect both air barrier and insulation installation criteria. Heated, attached private garage space and heated, detached private garage space shall be thermally isolated from all other habitable, conditioned spaces in accordance with Sections R402.2.13 and R402.4.5, as applicable.

Section R402.5.1.3 Maximum air leakage rate.

Section R402.5.1.3-Delete Section R402.5.1.3 in its entirety and add a new Section R402.5.1.3 to read as follows:

R402.5.1.3 Maximum air leakage rate. The maximum air leakage rate for any building under any compliance path shall not exceed 3.0    air changes per hour. Testing shall be conducted in accordance with ANSI/RESNET/ICC 380, ASTM E779 or ASTM E1827 and reported at a pressure differential of 0.2 inch water gauge (50 Pa).

Exception: Buildings over 50,000 square feet may comply with the testing requirements of section C402.6.

Section R402.5.1.4 Testing   procedure.

Section R402.1.4 - Add new Section R402.5.1.4, to read as follows:

R402.5.1.4 Testing   procedure.   Testing shall be conducted by an approved agency  . A written report of the results of the test shall be signed by the party conducting the test and provided to the building official. Testing shall be performed at any time after creation of all penetrations of the building thermal envelope have been sealed. The written report shall include:

1.  The name and place of business of the party conducting the test;

2.  The address of the building that was tested;

3.	The conditioned floor area of the dwelling, calculated in accordance with ANSI/BOMA Z65.1, except that conditioned floor area shall include areas where the ceiling height is less than 5 feet (1524 mm);

4.  Measurement of the air volume lost at an internal pressurization of 0.2 inches water gauge (50 Pa);

5.  The air leakage rate in air changes per hour or cubic feet per minute per square foot of dwelling unit enclosure area;

6.  The date(s) of the test;

7.  A certification by the party conducting the test of the accuracy of the test results; and

8.  The signature of the party conducting the test.

During testing:

1.  Exterior windows and doors, fireplace and stove doors shall be closed, but not sealed, beyond the intended weatherstripping or other infiltration control measures.

2.  Dampers including exhaust, intake, makeup air, backdraft and flue dampers shall be closed, but not sealed beyond intended infiltration control measures.

3.  Interior doors, where installed at the time of the test, shall be open.

4.  Exterior or interior terminations for continuous ventilation systems and heat recovery ventilators shall be closed and sealed.

5.  Heating and cooling systems, where installed at the time of the test, shall be turned off.

6. Supply and return registers, where installed at the time of the test, shall be fully open.

Section R402.6 Maximum fenestration U-factor and SHGC.

Section R402.6-Delete Section R402.6 in its entirety and add a new Section R402.6 to read as follows:

R402.6 Maximum fenestration U-factor and SHGC.   The area-weighted average maximum fenestration U-factor permitted using tradeoffs from Section R402.1.5 or R405 shall be 0.40 for vertical fenestration, and 0.72 for skylights.

Exception: The maximum U-factor and solar heat gain coefficient (SHGC) for fenestration shall not be required in storm shelters complying with ICC 500.

Section R402.7 Thermal bridges.

Section R402.7 – Add new Sections R402.7, R402.7.1, R402.7.2 and R402.7.3, and Table R402.7, to read as follows:

R402.7 Thermal bridges. Applications for construction document approval shall include documentation of thermal bridges.

R402.7.1 Clear field thermal bridges. Where otherwise not included in pre-calculated assembly U-factors, C-factors, or F-factors outlined in Appendix A of 2025 NYC ASHRAE 90.1, clear field thermal bridges in a wall, roof, or floor assembly shall be noted as such in the drawings.

R402.7.2 Point thermal bridges. Point thermal bridges greater than or equal in area to 8 in2 (5161 mm2) and not associated with HVAC or electrical systems shall be noted as thermal bridges in the drawings.

R402.7.3 Linear thermal bridges. Construction documents shall include the following documentation in tabular format for linear thermal bridges listed in Table R402.7:

1. Linear thermal bridge type.

2. Aggregate length of each type of linear thermal bridge.

3. Relevant detail in the construction documents showing a cross-section through the thermal bridge.

4. Ψ-value for each thermal bridge from Table R402.7.

Exception: Where linear thermal bridges have been tested or modeled using methods approved by the department, alternate values may be used as long as supporting documentation is provided

#### Table R402.7

#### AVERAGE THERMAL TRANSMITTANCE FOR UNMITIGATED LINEAR THERMAL BRIDGES

| Type of Thermal Bridge | Ψ-valuea [Btu/hr • ft • ˚F] | Ψ-valuea W/mK |
| --- | --- | --- |
| Steel Frame, Steel Stud, Poured-in-place Concrete, Concrete Block, Curtain-wall |  |  |
| Balcony | 0.50 | 0.871 |
| Floorb | 0.44 | 0.755 |
| Slab to Ground | n/a | n/a |
| Fenestration Perimeter Transitionc | 0.32 | 0.550 |
| Parapet | 0.42 | 0.735 |
| Eaves | n/a | n/a |
| Shelf Angle | 0.41 | 0.713 |
| Wood Frame Construction |  |  |
| Balcony | n/a | n/a |
| Floorb | 0.336 | 0.582 |
| Slab to Ground | n/a | n/a |
| Fenestration Perimeter Transitionc | 0.15 | 0.26 |
| Parapet | 0.032 | 0.056 |
| Eaves | n/a | n/a |
| Shelf Angle | 0.186 | 0.322 |

a.	Psi-values are derived from the ASHRAE Research Project 1365 and BC Hydro Building Envelope Thermal Bridging Guide Version 1.2 - September 2018, and are based on poor performing details.

b.	This value is for an intermediate floor. Ground to Slab thermal bridging is applicable for all buildings.

c.	Fenestration Perimeter Transition is the thermal bridge between any fenestration frame and the typical wall, roof or floor assembly it abuts or is mounted within. For each unique window or door installation type, provide a minimum of one typical-installation detail showing either the head, jamb or sill detail of the window or door frame and the abutting wall, roof or floor construction, including all structural and insulation layers, blocking, flashing, and cladding.

SECTION R403

SYSTEMS

Section R403.3.3 Ductwork located outside conditioned space.

Section R403.3.3 - Revise Section R403.3.3 to read as follows:

R403.3.3 Ductwork located outside conditioned space. New ductwork shall not be located outside conditioned space. Existing and return ductwork located outside conditioned space shall be insulated to an R-value of not less than R-8 for ducts 3 inches (76 mm) in diameter and larger and not less than R-6 for ducts smaller than 3 inches (76 mm) in diameter. Ductwork buried beneath a building shall be insulated. as required per this section or have an equivalent thermal distribution efficiency. Underground ductwork utilizing the thermal distribution efficiency method shall be listed and labeled to indicate the R-value equivalency.

Section R403.3.6 Sealing.

Section R403.3.6 - Revise Section R403.3.6 to read as follows:

R403.3.6 Sealing.  Ductwork, air-handling units and filter boxes shall be sealed. Joints and seams shall comply with either the New York City Mechanical Code, as applicable.

Section R403.4 Mechanical system piping insulation.

Section R403.4 - Revise Section R403.4 to read as follows:

R403.4 Mechanical system piping insulation.  Piping serving as part of a heating or cooling system capable of carrying fluids greater than 105°F (41°C) or less than 60°F (15°C) shall be thermally insulated in accordance with Table R403.4. The thickness and conductivity of the insulation must result in an R-value of not less than R-3.

Table R403.4 MINIMUM PIPE INSULATION THICKNESS (in inches).

Table R403.4 – Add Table R403.4.1 and Table R403.2 to read as follows:

TABLE R403.4.1

MINIMUM PIPE INSULATION THICKNESS (in inches)a, c

| FLUID OPERATING TEMPERATURE RANGE AND USAGE (°F) | INSULATION CONDUCTIVITY |  | INCHES OR R-VALUE | NOMINAL PIPE OR TUBE SIZE (inches) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Conductivity Btu × in./(h × ft2 × °F)b | Mean Rating Temperature, °F |  | < 1 | 1 to < 11/2 | 11/2 to < 4 | 4 to < 8 | > 8 |
| > 350 | 0.32–0.34 | 250 | Inches | 4.5 | 5.0 | 5.0 | 5.0 | 5.0 |
|  |  |  | R-value | R-32 | R-36 | R-34 | R-26 | R-21 |
| 251–350 | 0.29–0.32 | 200 | Inches | 3.0 | 4.0 | 4.5 | 4.5 | 4.5 |
|  |  |  | R-value | R-20 | R-29 | R-32 | R-24 | R-20 |
| 201–250 | 0.27–0.30 | 150 | Inches | 2.5 | 2.5 | 2.5 | 3.0 | 3.0 |
|  |  |  | R-value | R-17 | R-17 | R-17 | R-15 | R-13 |
| 141–200 | 0.25–0.29 | 125 | Inches | 1.5 | 1.5 | 2.0 | 2.0 | 2.0 |
|  |  |  | R-value | R-9 | R-9 | R-11 | R-10 | R-9 |
| 105–140 | 0.21–0.28 | 100 | Inches | 1.0 | 1.0 | 1.5 | 1.5 | 1.5 |
|  |  |  | R-value | R-5 | R-9 | R-8 | R-8 | R-7 |
| 40–60 | 0.21–0.27 | 75 | Inches | 0.5 | 0.5 | 1.0 | 1.0 | 1.0 |
|  |  |  | R-value | R-2 | R-2 | R-5 | R-5 | R-4 |
| < 40 | 0.20–0.26 | 50 | Inches | 0.5 | 1.0 | 1.0 | 1.0 | 1.5 |
|  |  |  | R-value | R-6 | R-9 | R-9 | R-8 | R-7 |

For SI: 1 inch = 25.4 mm, °C = [(°F) – 32]/1.8.

a.	For piping smaller than 11/2 inches and located in partitions within conditioned spaces, reduction of these thicknesses by 1 inch shall be permitted (before thickness adjustment required in Note b) but not to a thickness less than 1 inch.

b.	 For insulation outside the stated conductivity range, the minimum thickness (T) shall be determined as follows:

T = r[(1 + t/r)K/k – 1]

where:

T = Minimum insulation thickness.

r = Actual outside radius of pipe.

t = Insulation thickness listed in the table for applicable fluid temperature and pipe size.

K = Conductivity of alternate material at mean rating temperature indicated for the applicable fluid temperature (Btu × in/h × ft2 × °F).

k = The upper value of the conductivity range listed in the table for the applicable fluid temperature.

c.	For direct-buried heating and hot water system piping, reduction of these thicknesses by 11/2 inches (38 mm) shall be permitted (before thickness adjustment required in Note b but not to thicknesses less than 1 inch.

TABLE R403.4.2

MINIMUM PIPE INSULATION R-Valuea

| FLUID OPERATING TEMPERATURE RANGE AND USAGE (°F) | NOMINAL PIPE OR TUBE SIZE (inches) |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | <1 | 1 TO <1 1/2 | 1 1/2 TO <4 | 4 TO <8 | ≥8 |
|  | Minimum Insulation R-Value |  |  |  |  |
| >350 | R32 | R36 | R34 | R26 | R21 |
| 251-350 | R20 | R29 | R32 | R24 | R20 |
| 201-250 | R17 | R17 | R17 | R15 | R13 |
| 141-200 | R9 | R9 | R11 | R10 | R9 |
| 105-140 | R5 | R9 | R8 | R8 | R7 |
| 40-60 | R2 | R2 | R5 | R5 | R4 |
| ≤40 | R6 | R9 | R9 | R8 | R7 |

For SI: R-1 = RSI-0.176228, °C = [(°F)-32]/1.8.

a. The R-value of cylindrical piping insulation shall be determined as follows:

R=(ro(ln(ro/ri)))/k

where:

R = The interior R-value of the cylindrical piping insulation in Btu x ft2 x °F/h

ro = The outer radius of the piping insulation in inches

ri = The inner radius of the piping insulation in inches

k = the thermal conductivity of the insulation material in Btu x in/h x ft2 x °F

Section R403.5.3 Drain water heat recovery units.

Section R403.5.3 - Revise Section R403.5.3 to read as follows:

R403.5.3 Drain water heat recovery units.  Where installed, drain water heat recovery units shall have a minimum efficiency of 40 percent if installed for equal flow or a minimum efficiency of 52 percent if installed for unequal flow. Drain water heat recovery units shall comply with CSA B55.2 and be tested and labeled in accordance with CSA B55.1. Potable water-side pressure loss of drain water heat recovery units shall be less than 3 psi (20.7 kPa) for individual units connected to one or two showers. Potable water-side pressure loss of drain water heat recovery units shall be less than 2 psi (13.8 kPa) for individual units connected to three or more showers.

Section R403.5.5 Supply of service hot water.   .

Section R403.5.5 – Add Section R403.5.5, Table R403.5.5, Section R403.5.5.1, Table R403.5.5.1, Section R403.5.5.1.1, R403.5.5.2, R403.5.5.3, R403.5.5.4 and Table R403.5.5.4 to read as follows:

R403.5.5 Supply of heated water.   In new buildings, heated water supply piping shall be in accordance with one of the following:

1.Maximum allowable pipe length method. The maximum allowable pipe length from the nearest source of heated water to the termination of the fixture supply pipe shall be in accordance with the maximum pipe length in Table R403.5.5. Where the length contains more than one size of pipe, the largest size shall be used for determining the maximum allowable length of the piping in Table R403.5.5.

2.Maximum allowable pipe volume method. The water volume in the piping shall be calculated in accordance with Table R403.5.5. The maximum volume of hot or tempered water in the piping to public lavatory faucets shall be 2 ounces. For fixtures other than public lavatory faucets, the maximum volume shall be 64 ounces for hot or tempered water from a waterheater or boiler; and 24 ounces for hot or tempered water from a circulation loop pipe or an electrically heat-traced pipe

3.Drain water heat recovery units.  New buildings shall include a drain water heat recovery unit in accordance with R403.5.3.

4.Recirculation Systems. Projects shall include a recirculation system with no more than 0.5 gallon (1.9 liter) storage.  The storage limit shall be measured from the point where the branch feeding the fixture branches off the recirculation loop to the fixture.   Recirculation systems must be based on an occupant-controlled switch or an occupancy sensor, installed in each bathroom which is located beyond a 0.5 gallon stored-volume range from the water heater.

Table R403.5.5

Pipe Volume and Maximum Piping Lengths

| Nominal Pipe or Tube Size (inch) | VOLUME (Liquid Ounces Per Foot Length) | Maximum Pipe or Tube Length |  |
| --- | --- | --- | --- |
|  |  | System without a circulation loop or heat-traced line (feet) | System with a circulation loop or heat-traced line (feet) |
| 1/4a | 0.33 | 50 | 16 |
| 5/16a | 0.5 | 50 | 16 |
| 3/8a | 0.75 | 50 | 16 |
| 1/2 | 1.5 | 43 | 16 |
| 5/8 | 2 | 32 | 12 |
| 3/4 | 3 | 21 | 8 |
| 7/8 | 4 | 16 | 6 |
| 1 | 5 | 13 | 5 |
| 1 1/4 | 8 | 8 | 3 |
| 1 1/2 | 11 | 6 | 2 |
| 2 or larger | 18 | 4 | 1 |

a. The flow rate for ¼-inch size pipe or tube is limited to 0.5 gpm (0.032 (L/s); for 5/16-inch size, it is limited to 1 gpm (0.063 L/s); for 3/8-inch size, it is limited to 1.5 gpm (0.095 L/s).

b. The volume shall be the sum of the internal volumes of pipe, fittings, valves, meters and manifolds between the source of hot water and the termination of the fixture supply pipe. The volume contained within fixture shutoff valves, flexible water supply connectors to a fixture fitting, or within a fixture fitting shall not be included in the water volume determination. Where hot or tempered water is supplied by a circulation loop pipe or a heat-traced pipe, the volume shall include the portion of the fitting on the branch pipe that supplies water to the fixture.

Section R403.6 Mechanical ventilation.

Section R403.6 - Revise Section R403.6 to read as follows:

R403.6 Mechanical ventilation.  The buildings and dwelling units complying with Section R402.5.1.1 shall be provided with mechanical ventilation that complies with the requirements of the New York City Mechanical Code, as applicable, or with other approved means of ventilation. Outdoor air intakes and exhausts shall have automatic or gravity dampers that close when the ventilation system is not operating.

Section R403.6.1 Heat or energy recovery ventilation.

Section R403.6.1 - Revise Section R403.6.1 to read as follows:

R403.6.1 Heat or energy recovery ventilation.  Dwelling units shall be provided with a heat recovery or energy recovery ventilation system installed per manufacturer’s instructions.

Exception: A balanced ventilation system complying with the New York City Mechanical Code and sections R403.6.1.1 through R403.6.1.3 using the return side of the building’s heating and/or cooling system air handler to supply outdoor air, shall be permitted to comply with this section. When the outdoor air supply is ducted to the heating and/or cooling system air handler, the mixed air temperature shall not be less than that permitted by the heating equipment manufacturer’s installation instructions. Heating and/or cooling system air handlers used to distribute outdoor air shall be field-verified to not exceed an efficacy of 45 W/CFM if using furnaces for heating and 58 W/CFM if using other forms of heating.  In the balanced system design, an equivalent exhaust air flow rate shall be provided simultaneously by one or more exhaust fans, located remotely from the source of supply air. The balanced system’s exhaust and supply fans shall be interlocked for operation, sized to provide equivalent air flow at a rate greater than or equal to that determined by Table R403.6.1(1) and shall have their fan capacities adjusted for intermittent run time per Table R403.6.1(2). Continuous operation of the balanced ventilation system shall not be permitted.

Section R403.6.1.1 Whole-house mechanical ventilation (balanced ventilation option) system design.

Section R403.6.1.1 – Add new Section R403.6.1.1 to read as follows:

R403.6.1.1 Whole-house mechanical ventilation (balanced ventilation option) system design. The whole-house ventilation system shall consist of one or more supply or exhaust fans, or a combination of such, and associated ducts and controls. Local exhaust or supply fans are permitted to serve as such as system. Outdoor air ducts connected to the return side of an air handler shall be considered as providing supply ventilation.

Section R403.6.1.2 System controls.

Section R403.6.1.2 – Add new Section R403.6.1.2 to read as follows:

R403.6.1.2 System controls. The whole-house ventilation system shall be provided with controls that enable manual override.

Section R403.6.1.3 Mechanical ventilation rate.

Section R403.6.1.3 – Add new Section R403.6.1.3 to read as follows:

R403.6.1.3 Mechanical ventilation rate. The whole-house mechanical ventilation system is permitted to operate intermittently where the system has controls that enable operation for not less than 25 percent of each 4 hour segment and the ventilation rate prescribed in Table R403.6.1 (1) is multiplied by the factor determined in accordance with Table R403.6.1(2).

Table R403.6.1(1) Continuous Whole-House Mechanical Ventilation System Airflow Rate Requirements.

Table R403.6.1(1) – Add new Table R403.6.1(1) to read as follows:

TABLE R403.6.1(1) CONTINUOUS WHOLE-HOUSE MECHANICAL VENTILATION SYSTEM AIRFLOW RATE REQUIREMENTS

| DWELLING UNIT FLOOR AREA (square feet) | NUMBER OF BEDROOMS |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | 0 – 1 | 2 – 3 | 4 – 5 | 6 – 7 | > 7 |
|  | Airflow in CFM |  |  |  |  |
| < 1,500 | 30 | 45 | 60 | 75 | 90 |
| 1,501 – 3,000 | 45 | 60 | 75 | 90 | 105 |
| 3,001 – 4,500 | 60 | 75 | 90 | 105 | 120 |
| 4,501 – 6,000 | 75 | 90 | 105 | 120 | 135 |
| 6,001 – 7,500 | 90 | 105 | 120 | 135 | 150 |
| > 7,500 | 105 | 120 | 135 | 150 | 165 |

For SI: 1 square foot = 0.0929 m2, 1 cubic foot per minute = 0.0004719 m3/s

Table R403.6.1(2) Intermittent Whole-House Mechanical Ventilation Rate Factors.

Table R403.6.1(2) – Add new Table R403.6.1(2) to read as follows:

TABLE R403.6.1(2) INTERMITTENT WHOLE-HOUSE MECHANICAL VENTILATION RATE FACTORSa,b

| RUN-TIME PERCENTAGE IN EACH 4-HOUR SEGMENT | 25% | 33% | 50% | 66% | 75% | 100% |
| --- | --- | --- | --- | --- | --- | --- |
| Factora | 4 | 3 | 2 | 1.5 | 1.3 | 1.0 |

a.	For ventilation system run time values between those given, the factors are permitted to be determined by interpolation.

b.	Extrapolation beyond the table is prohibited.

Section R403.6.3 Testing.

Section R403.6.3 - Revise Section R403.6.3 to read as follows:

R403.6.3 Testing.  Mechanical ventilation systems shall be tested and verified to provide the minimum ventilation flow rates required by Section R403.6 in accordance with ANSI/RESNET/ICC 380. Testing shall be conducted by an approved agency.  A written report of the results of the test shall be signed by the party conducting the test and provided to the code official.

Exception:

1. Kitchen range hoods that are ducted to the outside with ducting having a diameter of 6-inches (152 mm) or larger, a length of 10 feet (3028 mm) or less duct and not more than two 90-degree (1.57 rad) elbows or equivalent shall not require testing.

2. A test by an approved agency shall not be required where the ventilation system has an integrated diagnostic tool used for airflow measurement, and a user interface that communicates the installed airflow rate.

3. Where tested in accordance with Section R403.6.4, testing of each mechanical ventilation system is not required.

Section R403.8 Systems serving multiple dwelling units.

Section R403.8 - Revise Section R403.8 to read as follows:

R403.8 Systems serving multiple dwelling units.  Except for systems complying with Section R403.9, systems serving multiple dwelling units shall comply with Sections C403 C404 and C408 of the New York City Energy Conservation Code instead of Section R403

Exception: Systems complying with Section R403.9

SECTION R404

SYSTEMS

Section R404.1.2 Exterior lighting power requirements.

Section R404.1.2  – Revise Section R404.1.2 to read as follows:

R404.1.2 Exterior lighting power requirements.  The total exterior connected lighting power shall be not greater than the exterior lighting power allowance calculated in accordance with Section R404.1.3. The total exterior connected lighting power shall be the total maximum rated wattage of all lighting that is powered through the energy service for the building .

Exceptions: Lighting used for the following applications shall not be included.

1.	Lighting approved for safety reasons.

2.	Emergency lighting that is automatically off during normal operations.

3.	Exit signs.

4.	Specialized signal, directional and marker lighting associated with transportation.

5.	Lighting for athletic playing areas.

6.	Temporary lighting.

7.	Lighting used to highlight features of art, public monuments and the national flag.

8.	Lighting for water features and swimming pools.

9.	Lighting controlled from within sleeping units and dwelling units.

10. Lighting of the exterior means of egress as required by the New York City Building Code.

Section R404.2.1 Habitable spaces.

Section R404.2.1 – Revise Section R404.2.1 to read as follows:

R404.2.1 Habitable spaces. All permanently installed luminaires in habitable spaces shall be controlled with a manual dimmer or with an automatic shutoff control that automatically turns off lights within 15 minutes after all occupants have left the space and shall incorporate a manual control to allow occupants to turn the lights on or off.

Section R404.5  Dwelling unit electrical meter.

Section R404.1 – Revise Section R403.3.3 to read as follows:

R404.5 Dwelling unit electrical meter.  In all buildings having individual dwelling units, provisions shall be made to determine the electrical energy consumed by each unit by separately metering individual dwelling units.

Section R404.8  Electrical vehicle service equipment capable.

Section R404.8 – Add new Section R404.8 to read as follows:

R404.8 Electrical vehicle service equipment capable. One or two-family dwellings and townhouses with parking area provided on the building site shall provide a 208/240V 40-amp outlet for each dwelling unit or panel capacity and conduit for the future installation of such an outlet. Outlet or conduit termination shall be adjacent to the parking area. For residential occupancies where there is a common parking area, provide either:

1. Panel capacity and conduit for the future installation of 208/240V 40-amp outlets for 5 percent of the total parking spaces, but not less than one outlet, or

2. 208/240V 40-amp outlets for 5 percent of the total parking spaces, but not less than one outlet.

SECTION R405

SIMULATED  BUILDING PERFORMANCE

Section R405.2 Simulated building performance compliance.

Section R405.2 – Revise Section R405.2 to read as follows:

R405.2 Simulated building performance compliance. Compliance based on simulated  building performance analysis requires that a building comply with the following:

1. The requirements of the sections indicated within Table R405.2.

2. The proposed total building thermal envelope thermal conductance (TCp) shall be less than or equal to the required total building thermal envelope TCr using the prescriptive U-factors and F-factors from Table R402.1.2 multiplied by 1.15 in accordance with Equation 4-2 and Section R402.1.5.

Equation 4-2 TCProposed design ≤ 1.15 × TCPrescriptive reference design

3. The annual site energy use expressed in Btu or Btu per square foot of conditioned floor area of the dwelling unit shall be less than or equal to 80 percent of the annual site energy use expressed in Btu or Btu per square foot of conditioned floor area of the standard reference design. For each dwelling unit with greater than 5,000 square feet (465 m2) of living space located above grade plane, the annual site energy use expressed in Btu or Btu per square foot of conditioned floor area of the dwelling unit shall be reduced by an additional 5 percent of annual site energy use expressed in Btu or Btu per square foot of conditioned floor area of the standard reference design.

SECTION R408

ADDITIONAL EFFICIENCY CREDITS

Section R408.2 Additional energy efficiency credit requirements.

Section R408.2 – Revise Section R408.2 to read as follows:

R408.2 Additional energy efficiency credit requirements.

Additional energy efficiency Residential buildings shall earn not less than 10 credits from not less than two measures specified in Table R408.2. Five additional credits shall be earned for buildings units with more than 5,000 square feet (465 m2) of living space located above grade plane. To earn credit as specified in Table R408.2 for the applicable climate zone, each measure selected for compliance shall comply with the applicable subsections of Section R408. Each dwelling unit or sleeping unit shall comply with the selected measure to earn credit. Interpolation of credits between measures shall not be permitted.

Table R408.2 Additional energy efficiency credit requirements.

Table R408 2 – Revise Table  R408.2 to read as follows:

TABLE R408.2  CREDITS FOR ADDITIONAL ENERGY EFFICIENCY

| MEASURE NUMBER | MEASURE DESCRIPTION |  |  |  |
| --- | --- | --- | --- | --- |
|  |  | Climate Zone 4 | Climate Zone 5 | Climate Zone 6 |
| R408.2.1.1(1) | ≥ 2.5% Reduction in total TC | 1 | 1 | 1 |
| R408.2.1.1(2) | ≥ 5% reduction in total TC | 2 | 2 | 2 |
| R408.2.1.1(3) | > 7.5% reduction in total TC | 2 | 2 | 3 |
| R408.2.1.1(4) | > 10% reduction in total TC | 3 | 4 | 4 |
| R408.2.1.1(5) | > 15% reduction in total TC | 4 | 5 | 6 |
| R408.2.1.1(6) | > 20% reduction in total TC | 5 | 7 | 8 |
| R408.2.1.1(7) | > 30% reduction in total TC | 8 | 11 | 12 |
| R408.2.1.2(1) | U-factor and SHGC for vertical fenestration per Table R408.2.1.2 | 2 | 1 | 1 |
| R408.2.1.4 | Reduced air leakage | 2 | 3 | NA |
| R408.2.2(1)b | Ground source heat pump | 15 | 15 | 17 |
| R408.2.2(2)b | High Performance Cooling (Option 1) | 2 | 1 | 1 |
| R408.2.2(3)b | High Performance Cooling (Option 2) | 2 | 1 | 1 |
| R408.2.2(10)b | High Performance Heat pump with electric resistance backup (Option 1) | 12 | NA | NA |
| R408.2.2(14)b | High Performance Heat pump with electric resistance backup (Option 2) | 12 | 12 | 13 |
| R408.2.3(3)d | Electric water heaters (Option 1) | 7 | 4 | 3 |
| R408.2.3(4)d | Electric water heaters (Option 2) | 6 | 4 | 3 |
| R408.2.3(5)(a)d | Electric water heaters (Option 3) | 6 | 5 | 4 |
| R408.2.3(5)(b)d | Electric water heaters (Option 4) | 7 | 5 | 5 |
| R408.2.3(6)d | Electric water heaters (Option 5) | 7 | 4 | 3 |
| R408.2.3(7)(a)d | Solar hot water heating system (Option 1) | 9 | 5 | 4 |
| R408.2.3(7)(b)d | Solar hot water heating system (Option 2) | 6 | 6 | 5 |
| R408.2.4(1)c | Ductless or hydronic thermal distribution | 7 | 10 | 10 |
| R408.2.4(2)c | 100% of duct systems in conditioned space | 6 | 9 | 9 |
| R408.2.4(3)c | ≥ 80% of ductwork inside conditioned space | 5 | 7 | 7 |
| R408.2.4(4)c | Reduced total duct system leakage | 1 | 1 | 2 |
| R408.2.5(2)c | ≤ 2.0 ACH50 with ERV or HRV installed | 4 | 8 | 5 |
| R408.2.5(4)c | ≤ 1.5 ACH50 with ERV or HRV installed | 6 | 10 | 9 |
| R408.2.5(5)c | ≤ 1.0 ACH50 with ERV or HRV installed | 7 | 12 | 12 |
| R408.2.6a | Embodied Carbon | 1 | 1 | 0 |
| R408.2.7 | On-site renewable energy measures | 11 | 9 | 8 |
| R408.2.8c | Demand responsive thermostat | 1 | 1 | 1 |

NA = Not Applicable.

a.   Where the measure is selected, each dwelling unit, sleeping unit and common area where the measure is applicable must have the measure installed.

b.  Where multiple heating or cooling systems are installed, credits shall be determined using a weighted average of the square footage served by each system.

c.   Where the measure is selected, each dwelling unit and sleeping unit must comply with the measure.

d.  Where the measure is selected, each dwelling unit shall be served by a water heater meeting the applicable requirements. Where multiple service water heating systems are installed, credits shall be determined using a weighted average of the square footage served by each system.

e.   Eleven credits are available for Climate Zone 4 where the following measure is used: gas furnace and heat pump (Option 3): greater than or equal to 95% AFUE fuel gas furnace and 7.8 HSPF2, 15.2 SEER2 and 10.0 EER2 air source heat pump.

Section R408.2.1.3 Roof solar reflectance index.

Section R408.2.1.3 – Revise Section R408.2.1.3 to read as follows:

R408.2.1.3 Roof solar reflectance index. Reserved.

Section R408.2.1.3.1 Aged solar reflectance..

Section R408.2.1.3.1 – Revise Section R408.2.1.3.1 to read as follows:

R408.2.1.3.1 Aged solar reflectance. Reserved.

Section R408.2.2 More efficient HVAC equipment performance options.

Section R408.2.2 – Revise Section R408.2.2 to read as follows:

R408.2.2 More efficient HVAC equipment performance options. Heating and cooling equipment shall meet one of the following measures as applicable for the climate zone where heating and cooling efficiencies are represented by Annual Fuel Utilization Efficiency (AFUE), Coefficient of Performance (COP), Energy Efficiency Ratio (EER and EER2), Heating Season Performance

Factor (HSPF2) and Seasonal Energy Efficiency Ratio (SEER2). Where multiple heating or cooling systems are installed serving different zones, credits shall be earned based on the weighted average of square footage of the zone served by the system.

HVAC options:

1. Ground source heat pump: Greater than or equal to 16.1 EER and 3.1 COP ground source heat pump.

2. Cooling (Option 1): Greater than or equal to 15.2 SEER2 and 12.0 EER2 air conditioner.

3. Cooling (Option 2): Greater than or equal to 16.0 SEER2 and 12.0 EER2 air conditioner.

4. Heat pump (Option 2): Greater than or equal to 8.1 HSPF2 and 15.2 SEER2 air source heat pump capable of meeting a capacity ratio ≥ 70 percent of heating capacity at 5°F (-15°C) versus rated heating capacity at 47°F (8.3°C).

Section R408.2.2.1 More efficient HVAC equipment for Climate Zone 4.

Section R408.2.2.1 – Revise Section R408.2.2.1 to read as follows:

R408.2.2.1 More efficient HVAC equipment for Climate Zone 4. For Climate Zone 4, the following HVAC option shall also apply:

1. Heat pump (Option 1): Greater than or equal to 7.8 HSPF2, 15.2 SEER2 and 11.7 EER2 air source heat pump.

Table R408.2.3 Additional energy efficiency credit requirements..

Table R408.2.3 – Revise Table  R408.2.3 to read as follows:

TABLE R408.2.3—SERVICE WATER HEATING EFFICIENCIES

| MEASURE NUMBER | WATER HEATER | SIZE AND DRAW PATTERN | TYPE | EFFICIENCY |
| --- | --- | --- | --- | --- |
| R408.2.3(3) | Electric water heaters (Option 1) | All storage volumes, low, medium, or high | Integrated HPWH | UEF ≥ 3.30 |
| R408.2.3(4) | Electric water heaters (Option 2) | All storage volumes, low, medium, or high | Integrated HPWH, 120 volt/15 amp circuit | UEF ≥ 2.20 |
| R408.2.3(5)(a) | Electric water heaters (Option 3) | All storage volumes, low, medium, or high | Split-system HPWH | UEF ≥ 2.20 |
| R408.2.3(5)(b) | Electric water heaters (Option 4) | All storage volumes, low, medium, or high | Split-system HPWH | UEF ≥ 3.75 |
| R408.2.3(6) | Electric water heaters (Option 5) | Rated input capacity > 12 kW | — | COP ≥ 3.00 |
| R408.2.3(7)(a) | Solar water heaters (Option 1) | All storage volumes, all draw patterns | Electric backup | SUEF ≥ 3.00 |
| R408.2.3(7)(b) | Solar water heaters (Option 2) | All storage volumes, all draw patterns | Gas backup | SUEF ≥ 1.80 |

For SI: 1 British thermal unit per hour = 0.2931 W.

UEF = Uniform Energy Factor, Et = Thermal Efficiency, COP = Coefficient of Performance.

Section R408.2.3.1 Compact hot water distribution system option.

Section R408.2.3.1 – Revise Section R408.2.3.1 to read as follows:

R408.2.3.1 Compact hot water distribution system option. Reserved.

Section R408.2.3.1.1 Water volume determination.

Section R408.2.3.1.1 – Revise Section R408.2.3.1.1 to read as follows:

R408.2.3.1.1 Water volume determination. Reserved.

Section R408.2.6 Energy efficient appliances.

Section R408.2.6 – Revise Section R408.2.6 to read as follows:

R408.2.6 Embodied Energy/Carbon Tracking. Where the following building materials are used, the applicant shall provide documentation as described below in order to obtain a credit for additional energy efficiency;

1.	Concrete Masonry Units . To obtain a credit for Embodied Energy/Carbon Tracking for Concrete Masonry Units, the applicant shall include the following information as part of the Energy Analysis submitted with the construction documentation:

1.1	Environmental Product Declaration (EPD) for the proposed product showing the embodied carbon of the CMU product (Units: Units:  kgCO2e/m3)

1.2	The listed embodied carbon of the CMU product per the EPD (Units:  kgCO2e/m3);

1.3	The total quantity (Units: m3) of the CMU in the project;

1.4	The total embodied carbon of CMU (listed embodied carbon multiplied by quantity) in the project versus the baseline embodied carbon of CMU (industry wide baseline embodied carbon multiplied by quantity);

1.4.1 Industry Wide Baseline Embodied Carbon for Concrete Masonry Unit: 177 kgC02e/yr

1.5	The application does NOT need to demonstrate a reduction in embodied carbon from the baseline in order to obtain the credit;

2.	 Poured in Place Concrete: To obtain a credit for Embodied Energy/Carbon Tracking for Poured in Place Concrete, the applicant shall include the following information as part of the Energy Analysis submitted with the construction documentation:

2.1	The type and specified compressive strength (psi) of the poured in place concrete

2.2	Environmental Product Declaration (EPD) for the proposed concrete showing the embodied carbon of the CMU product (Units: Units:  kgCO2e/m3)

2.3	The listed embodied carbon of the poured in place concrete per the EPD (Units:  kgCO2e/m3);

2.4 The total quantity (Units: y3) of the poured in place concrete in the project;

2.5 The total embodied carbon of poured in place concrete (listed embodied carbon multiplied by quantity) in the project versus the baseline embodied  carbon of poured in place concrete (industry wide baseline embodied carbon multiplied by quantity);

2.5.1	Industry Wide Baseline Embodied Carbon for Poured in Place Concrete (Ready Mix)

-	0-2500 psi: 175 kgCO2e/y3

-	2501-3000 psi: 194 kgCO2e/y3

-	3001-4000 psi:  238 kgCO2e/y3

-	4001-5000 psi:  289 kgCO2e/y3

-	5001-6000 psi: 304 kgCO2e/y3

-	6001-8000 psi:  353kgCO2e/y3

2.5.2	Industry Wide Baseline Embodied Carbon for Poured in Place Concrete (Lightweight Concrete)

-	0-3000 psi: 365 kgCO2e/y3

-	3001-4000 psi: 417 kgCO2e/y3

-	4001-5000 psi:  461 kgCO2e/y3

2.6	The application does NOT need to demonstrate a reduction in embodied carbon from the baseline in order to obtain the credit;

Table R408.2.6 Minimum Efficiency Requirements: Appliances.

Table R408.2.6 – Delete  Table  R408.2.6 in its entirety.

Section R408.2.7 Renewable energy.

Section R408.2.7 – Revise Section R408.2.7 to read as follows:

R408.2.7 Renewable energy. Renewable energy resources shall be permanently installed and have the rated capacity to produce not less than 1.0 watt of on-site renewable energy per square foot of conditioned floor area. To qualify for this option, renewable energy certificate (REC) documentation shall meet the requirements of Section R404.4. This credit is only applicable for renewable energy infrastructure that exceeds the requirements of any current state or local law, rule or regulation..

Section R408.2.7 Renewable energy.

Section R408.2.7 – Revise Section R408.2.7 to read as follows:

R408.2.9 Opaque walls. Reserved.

# CHAPTER R5

EXISTING BUILDINGS

SECTION R501

GENERAL

Section R501.1 Scope.

Section R501.1 – Revise Section R501.1 to read as follows:

R501.1 Scope.  The provisions of this chapter shall control the alteration, repair, addition and change of occupancy of existing buildings and structures. This chapter shall not apply to alterations required to comply with new building provisions as determined by 28-101.4.5 of the New York City Administrative Code.

Section R501.2 Compliance.

Section R501.2 – Revise Section R501.2 to read as follows:

R501.2 Compliance. Additions, alterations, repairs or changes of occupancy to, or relocation of, an existing building, building system or portion thereof shall comply with Section R502, R503, R504 or R505, respectively, in this code, and the provisions for alterations, repairs, additions and changes of occupancy or relocation, respectively, in the New York City Building Code, the New York City Fire Code, the New York City Fuel Gas Code, the New York City Mechanical Code, the New York City Plumbing Code, the Housing Maintenance Code and the New York City Electrical Code. as applicable. Changes where unconditioned space is changed to conditioned space shall comply with Section R501.6.

SECTION R502

ADDITIONS

Section R502.1 General.

Section R501.2 – Revise Section R501.2 to read as follows:

R502.1 General.  Additions to an existing building, building system or portion thereof shall conform to the provisions of this code as those provisions relate to new construction Additions shall not create an unsafe or hazardous condition or overload existing building systems.  Altered portions of the building filed in conjunction with an addition shall comply with section R503.

Section R502.2.1 Building thermal envelope.

Section R502.2.1 – Revise Section R502.2.1 to read as follows:

R502.2.1 Building thermal envelope.  New building thermal envelope assemblies that are part of the addition shall comply with Sections R402.1, R402.2, R402.4.1 through R402.4.5, and R402.5.

Exceptions:

1.Section R402.5.1.2 shall only require testing of the portion of the envelope that is part of the addition in accordance with the guarded test provisions of ANSI/RESNET/ICC 380.

2. For additions less than 10 percent of the existing building conditioned area, the commissioner may waive the requirements of section R402.5.1.2 by having a Registered Design Professional submit an analysis indicating that such test would not significantly impact the energy performance of the addition.

Section R502.2.2 Heating and cooling systems.

Section R502.2.2 – Revise Section R502.2.2 to read as follows:

R502.2.2 Heating and cooling systems.

New heating, cooling, ventilation systems and ductwork that are part of an addition shall comply with Section R403.

Exception: Where ductwork from an existing heating and cooling system is extended to an addition, Sections R403.3.7 and R403.3.8 shall not be required for those portions of the systems that have not been modified.

Section R502.2.5 Additional energy efficiency credit requirements for additions.

Section R502.2.5 – Delete Section R502.2.5 in its 2 in its entirety.

SECTION R503

ALTERATIONS

Section R503.1.1.3 Above-grade wall alterations.

Section R503.1.1.3 – Revise Section R503.1.1.3 to read as follows:

R503.1.1.3 Above-grade wall alterations. Above-grade wall alterations shall comply with the following as applicable:

1. Where wall cavities are exposed, the exposed cavities shall be insulated to full depth with new or existing insulation that complies with Section R303.1.4 and having a minimum nominal value of R-3.5   per inch. New cavities created shall be insulated in accordance with Section R402.1. An interior vapor retarder shall be provided where required in accordance with chapter 14 of the New York City Building Code.

2. Where exterior wall coverings, recladding   and fenestration are added or replaced for the full extent of any exterior facade of one or more elevations of the building , continuous insulation shall be provided where required in accordance with Section R402.1. Where specified, the continuous insulation requirement also shall comply with the requirements of chapter 14 of the New York City Building Code as applicable, and manufacturers’ instructions.

3. Where new interior finishes or exterior wall coverings are applied to the full extent of any exterior wall assembly of mass construction, insulation shall be provided in accordance with Section R402.1.

Section R503.1.1.4 Floor alterations.

Section R503.1.1.3 – Revise Section R503.1.1.3 to read as follows:

R503.1.1.4 Floor alterations.    Where cavities in a floor or floor overhang are exposed and the floor or floor overhang is part of the building thermal envelope, the cavities shall be insulated to full depth with new or existing insulation that complies with Section R303.1.4. and having a minimum nominal value of R-3.5   per inch. New cavities created in the floor or floor overhang shall comply with Section R402.1. Where an unconditioned below-grade space is changed to conditioned space, floors that are part of the building thermal envelope enclosing such space shall comply with Section R502.

Section R503.1.1.6 Air barrier.

Section R503.1.1.6 – Revise Section R503.1.1.6 to read as follows:

R503.1.1.6 Air barrier. Altered building thermal envelope assemblies shall be provided with an air barrier in accordance with Section R402.5. The air barrier shall be made continuous with an existing air barrier where present in adjacent assemblies provided access is unobstructed. Testing requirements of Section R402.5.1.2 shall not be required.

Section R503.1.2 Heating and cooling systems.

Section R503.1.2 – Revise Section R503.1.2 to read as follows:

R503.1.2 Heating and cooling systems.

New heating, cooling, ventilation systems and ductwork that are part of the alteration shall comply with Section R403 and this section. Alterations to existing heating and cooling systems and ductwork shall comply with this section.

Exception: Where ductwork from an existing heating and cooling system is extended, Sections R403.3.7 and R403.3.8 shall not be required for those portions of the systems that have not been modified

Section R503.1.2.1 Ductwork.

Section R503.1.2.1 – Revise Section R503.1.2.1 to read as follows:

R503.1.2.1 Ductwork.

HVAC ductwork newly installed as part of an alteration shall comply with Section R403.

Exception: Sections R403.3.7 and R403.3.8 shall not be required for those portions of the systems that have not been modified.

Section R503.1.3 Service hot water systems.

Section R503.1.3 – Revise Section R503.1.3 to read as follows:

R503.1.3 Service hot water systems.  New service hot water systems that are part of the alteration shall comply with Section R403.5.

Exception: Existing buildings complying with this section are exempt if the section requires altering existing systems withing the building.

§ 28-1001.2.2  New York city amendments to the New York State-specific version of ASHRAE 90.1.

2025 NYC ASHRAE 90.1

Section 3.1.1 Occupancy.

Section 3.1.1 – Add new Section 3.1.1 to read as follows:

3.1.1 Occupancy. Occupancy classification and use shall be determined by Chapter 3 of the NYC Building Code.

Section 3.2 Definitions.

Section 3.2  – Delete the definition of  “authority having jurisdiction,” after the definition of “attic and other roofs.” .

Section 3.2  – Add the definition of  “authority having jurisdiction,” after the definition of “attic and other roofs.” to read as follows:

authority having jurisdiction: the commissioner or the commissioner's designee.

Section 3.2  – Add the definition of  “clear-field U-factor”     after the definition of “clear-field thermal bridge.” to read as follows:

clear-field U-factor. thermal performance factor that accounts for clear-field thermal bridges.

Section 3.2  – Add the definition of  “demand responsive control,”  “ demand response signal”  after the definition of “demand control ventilation (DCV).” to read as follows:

demand responsive control: a control capable of receiving and automatically responding to a demand response signal.

demand response signal: a signal that indicates a price or a request to modify electricity consumption for a limited time period.

Section 3.2  – Delete the definition of  “labeled” after the definition of “kilowatt (kW)” .

Section 3.2  – Add the definition of  “labeled” after the definition of “kilowatt (kW)” to read as follows:

labeled: See Section 28-101.5 of the Administrative Code.

Section 3.2 – Add the definitions of “Pre-Engineered Metal Building,”    after the definition of “primary sidelighted area” to read as follows:

PRE-ENGINEERED METAL BUILDING. A pre-engineered metal building (PEMB) is a structure where the steel components—primary framing, secondary framing, and cladding—are designed and manufactured in a factory according to specific project requirements and then shipped to the construction site for assembly.

Section 3.2  – Add the definition of  “spandrel panel” after the definition of “space conditioning category” to read as follows:

spandrel panel:  an opaque assembly within a fenestration framing system in a wall that is part of the building thermal envelope. Such panels are considered to be a portion of the opaque thermal envelope assembly.

Section 4 - Administration and Enforcement

Section 4.2.1.1 New Buildings

Section 4.2.1.1 - Delete Section 4.2.1.1 in its entirety, and replace with a new Section 4.2.1.1 to read as follows:

4.2.1.1 New Buildings

New buildings shall comply with Sections 4.2.2 through 4.2.5 and either the provisions of

a. Sections 5, “Building Envelope”; 6, “Heating, Ventilating, and Air Conditioning”; 7, “Service Water Heating”; 8, “Power”; 9, “Lighting”; 10, “Other Equipment,” and 11, “Additional Efficiency Requirements or

b. Section 12, “Energy Cost Budget Method,” or

c. Normative Appendix G, “Performance Rating Method.”

When using Normative Appendix G, of new buildings, additions to existing buildings, and/or alterations shall comply with Section 4.2.1.1.1 and Section 4.2.1.1.2. Alterations to existing buildings shall comply with Section 4.2.1.1.1.

Section 5 - Building Envelope.

Section 5.4.3.1.1

Section 5.4.3.1.2 - Delete Section 5.4.3.1.1 in its entirety, and replace with a new Section 5.4.3.1.1 to read as follows:

5.4.3.1.1

New buildings shall comply with measured air leakage requirements in Section 5.4.3.1.4 and continuous air barrier design and installation verification program performed in accordance with Section 5.9.1.2.

Section 5.4.3.1.2

Section 5.4.3.1.2 - Delete Section 5.4.3.1.2 in its entirety, and replace with a new Section 5.4.3.1.2 to read as follows:

5.4.3.1.2

Reserved

Section 5.4.3.1.4 Measured Air Leakage

Section 5.4.3.1.4 - Delete Section 5.4.3.1.4 in its entirety, and replace with a new Section 5.4.3.1.4 to read as follows:

5.4.3.1.4 Measured Air Leakage.

Where measured air leakage is used for compliance, the rate of air leakage of the building envelope shall not exceed 0.35 cfm/ft2 (1 L/s/m2) under a pressure differential of 75 Pa (0.30 in. of water), with this air leakage rate normalized by the sum of the above-grade and below-grade building envelope areas of the conditioned space and semiheated space and in accordance with this section.

a. Whole-building pressurization testing shall be conducted in accordance with ASTM E3158, ASTM E779 or ASTM E1827. Air leakage shall be measured following a multi-point regression method and then averaged from depressurization and pressurization tests.

For buildings greater than 50,000 square feet (4,645 m2), portions of the building shall be permitted to be tested following the procedures for a guarded test in ASTM E3158 and the measured air leakage shall be area-weighted by the surface areas of the building thermal envelope in each portion. The weighted average tested air leakage shall not be greater than the whole building leakage limit. The following portions of the building shall be tested:

1.1	The entire building thermal envelope area of stories that have any conditioned spaces directly under a roof.

1.2	The entire building thermal envelope area of stories that have a building entrance, have a floor over unconditioned space, have a loading dock, or that are below grade.

1.3	Representative above-grade portions of the building totaling not less than 25 percent of the wall area enclosing the remaining conditioned space.

Exception to 5.4.3.1.4(a)

Hospital, Museums and other occupancies approved by the commissioner may be permitted to only perform pressurization test to comply with the requirements of this section.

b. Where a building contains both conditioned space and semiheated space, compliance shall be shown using one of the following as applicable:

1. Separately for the conditioned space and for the semiheated space, with the air leakage rate for the conditioned space normalized by the exterior building envelope area of the conditioned space and the air leakage rate for the semiheated space normalized by the semiexterior building envelope area of the semiheated space

2. For the conditioned space and for the semiheated space together, with the air leakage rate for the overall space normalized by the sum of the exterior building envelope area and the semiexterior building envelope area minus the semiexterior building envelope area that separates the conditioned space from the semiheated space

c. Reporting shall be in compliance with Section 4.2.5.1.2.

Section 5.5.3	Opaque Elements.

Section 5.5.3 - Delete Section 5.5.3 in its entirety, and replace with a new Section 5.5.3 to read as follows:

5.5.3 Opaque Elements.

For all opaque, elements compliance with Tables 5.5-4 and  5.5-5 for each class of construction as described in Normative Appendix A, Sections A2 through A8 shall be demonstrated by one of the following two methods:

a.	Providing a minimum rated R-value of insulation added to the assembly equal to or greater than the insulation minimum R-value required of each insulation component.

b.	Providing insulation such that the maximum U-factor, C-factor, or F-factor for the entire assembly is not exceeded as determined by one of the following:

1. Precalculated values in accordance with Normative Appendix A, Section A1.1.

2. Applicant-determined values in accordance with Normative Appendix A, Section A1.2 where such values are approved by the building official.

Exceptions to 5.5.3

1.	For opaque assemblies not complying with the classes of construction as described in Normative Appendix A, Sections A2 through A8, compliance with the maximum U-factors for the “attic and other” or “wood frame and other” opaque element conditions in Tables 5.5-4 and Table 5.5-5 shall be demonstrated by testing or calculations in accordance with Normative Appendix A, Section A9.1 where approved by the building official.

2.	For multiple assemblies within a single class of construction for a single space conditioning category, compliance shall be shown for either (a) the most restrictive requirement or (b) an area-weighted average U-factor, C-factor, or F-factor.

3.	When the total area of penetrations from through-the-wall equipment or equipment listed in Table 6.8.1-4 exceeds 1% of the opaque above-grade wall area, the mechanical equipment penetration area shall be calculated as a separate wall assembly with a default U-factor of 0.5, and compliance shall be shown with method b of this section. Where mechanical equipment has been tested in accordance with testing standards, approved by the authority having jurisdiction, the mechanical equipment penetration area may be calculated as a separate wall assembly with the U-factor as determined by such test.

4.	For opaque assemblies in curtain wall framing or other fenestration framing systems, compliance shall be shown using the effective U-factor values of Table 5.5.3

Table 5.5.3 Effective U-factors for Spandrel Panels and Glass Curtain Wallsa.

Table 5.5.3 - Add a new Table 5.5.3 to read as follows:

Table 5.5.3 Effective U-factors for Spandrel Panels and Glass Curtain Wallsa

| RATED R-VALUE OF INSULATION BETWEEN FRAMING MEMBERS |  | None | R-4 | R-7 | R-10 | R-15 | R-20 | R-25 | R-30 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Frame Type | Spandrel Panel | Default U-factor |  |  |  |  |  |  |  |
| Aluminum without thermal breakb | Single glass pane, stone, or metal panel | U-0.445 | U-0.285 | U-0.259 | U-0.247 | U-0.236 | U-0.230 | U-0.226 | U-0.224 |
|  | Double glazing with no low-e coatings | U-0.356 | U-0.273 | U-0.254 | U-0.244 | U-0.234 | U-0.229 | U-0.226 | U-0.223 |
|  | Triple glazing or double glazing with low-e glass | U-0.313 | U-0.263 | U-0.249 | U-0.241 | U-0.233 | U-0.228 | U-0.225 | U-0.223 |
| Aluminum with thermal breakc | Single glass pane, stone, or metal panel | U-0.429 | U-0.243 | U-0.212 | U-0.197 | U-0.184 | U-0.176 | U-0.172 | U-0.169 |
|  | Double glazing with no low-e coatings | U-0.328 | U-0.228 | U-0.205 | U-0.193 | U-0.182 | U-0.175 | U-0.171 | U-0.168 |
|  | Triple glazing or double glazing with low-e glass | U-0.277 | U-0.217 | U-0.199 | U-0.189 | U-0.180 | U-0.174 | U-0.170 | U-0.167 |
| Structural glazingd | Single glass pane, stone, or metal panel | U-0.428 | U-0.217 | U-0.180 | U-0.161 | U-0.145 | U-0.136 | U-0.130 | U-0.126 |
|  | Double glazing with no low-e coatings | U-0.316 | U-0.199 | U-0.172 | U-0.157 | U-0.143 | U-0.135 | U-0.129 | U-0.126 |
|  | Triple glazing or double glazing with low-e glass | U-0.257 | U-0.186 | U-0.165 | U-0.152 | U-0.140 | U-0.133 | U-0.128 | U-0.125 |
| No framing or insulation is continuouse | Single glass pane, stone, or metal panel | U-0.445 | U-0.160 | U-0.108 | U-0.082 | U-0.058 | U-0.045 | U-0.037 | U-0.031 |
|  | Double glazing with no low-e coatings | U-0.356 | U-0.147 | U-0.102 | U-0.078 | U-0.056 | U-0.044 | U-0.036 | U-0.030 |
|  | Triple glazing or double glazing with low-e glass | U-0.313 | U-0.139 | U-0.098 | U-0.076 | U-0.055 | U-0.043 | U-0.035 | U-0.030 |

a .Extrapolation outside of the table and interpolation between values in the table shall not be permitted. Assemblies with distance between framing less than 30 inches (762 mm), or not included in the default table, shall have a U-factor determined by testing in compliance with ASTM C1363 or modeling in compliance with ANSI/NFRC 100. Spandrel panel assemblies in the table do not include metal backpans. For designs with metal backpans, multiply the U-factor by 1.20. U-factors for spandrel panels include a 3/4 in. air gap and 5/8 in. gypsum board with Rvalue of 0.56 for the interior finish. The gypsum board is assumed to span between the window sill and a channel at the floor.

b. This frame type shall be used for systems that do not contain a non-metallic element that separates the metal exposed to the exterior from the metal that is exposed to the interior condition.

c. This frame type shall be used for systems where a urethane or other non-metallic element separates the metal exposed to the exterior from the metal that is exposed to the interior condition.

d. This frame type shall be used for systems that have no exposed mullion on the interior exterior.

e This frame type shall be used for systems where there is no framing, or the insulation is continuous across and uninterrupted by the framing (also known as mullion wrap).

Table 5.5-4 Building Envelope Requirements for Climate Zone 4 (A,B,C)*

Table 5.5-4- Revise Table 5.5-4 to read as follows:

Table 5.5-4 Building Envelope Requirements for Climate Zone 4 (A,B,C)*

|  | Nonresidential |  |  | Residential |  |  | Semiheated |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Opaque Elements | Assembly Maximum |  | Insulation Min. R-Value | Assembly Maximum |  | Insulation Min. R-Value | Assembly Maximum |  | Insulation Min. R-Value |  |
| Roofs |  |  |  |  |  |  |  |  |  |  |
| Insulation entirely above deck | U-0.030 |  | R-33 c.i | U-0.030 |  | R-33 c.i. | U-0.093 |  | R-10 c.i. |  |
| Pre-Engineered Metal buildinga | U-0.035 |  | R-19 + R-11 Ls or or R-25 + R-8 Ls | U-0.035 |  | R-19 + R-11 Ls or R-25 + R-8 Ls | U-0.082 |  | R-19 |  |
| Attic and other | U-0.020 |  | R-49ca | U-0.020 |  | R-49ca | U-0.034 |  | R-30 |  |
| Walls, above Grade |  |  |  |  |  |  |  |  |  |  |
| Mass | U-0.099 |  | R-11.2 c.i | U-0.086 |  | R-13.25 c.i. | U-0.580 |  | NR |  |
| Pre-Engineered Metal building | U-0.048 |  | R-13ca + R-14.9 c.i. | U-0.048 |  | R-13ca + R-14.9 c.i. | U-0.162 |  | R-13 |  |
| Steel-framed | U-0.061 |  | R-13ca + R-8.5 c.i. | U-0.061 |  | R-13ca + R-8.5 c.i | U-0.124 |  | R-13 |  |
| Wood-framed and other | U-0.061 |  | R-13ca + R-4.5 c.i. or R-19ca+R-1.5ci | U-0.061 |  | R-13ca + R-4.5 c.i. or R-19ca+R-1.5ci | U-0.089 |  | R-13 |  |
| Wall, below Grade |  |  |  |  |  |  |  |  |  |  |
| Below-grade wall | C-0.119 |  | R-7.5 c.i. | C-0.092 |  | R-10 c.i. | C-1.140 |  | NR |  |
| Floors |  |  |  |  |  |  |  |  |  |  |
| Mass | U-0.057 |  | R-14.6 c.i. | U-0.051 |  | R-16.7 c.i. | U-0.107 |  | R-6.3 c.i. |  |
| Steel joist | U-0.033 |  | R-38ca | U-0.033 |  | R-38ca | U-0.052 |  | R-19 |  |
| Wood-framed and other | U-0.033 |  | R-30ca | U-0.033 |  | R-30ca | U-0.051 |  | R-19 |  |
| Slab-on-Grade Floors |  |  |  |  |  |  |  |  |  |  |
| Unheated | F-0.520 |  | R-15 for 24 in. | F-0.520 |  | R-15 for 24 in. | F-0.730 |  | NR |  |
| Heated | F-0.843 |  | R-20 for 48 in. +%-5 full slab | F-0.63 |  | R-20 for 48 in.+R-5 full slab | F-0.900 |  | R-10 for 24 in. |  |
| Opaque Doors |  |  |  |  |  |  |  |  |  |  |
| Swinging | U-0.370 |  |  | U-0.370 |  |  | U-0.370 |  |  |  |
| Nonswinging | U-0.310 |  |  | U-0.310 |  |  | U-0.360 |  |  |  |
| Fenestration | Assembly Max. U | Assembly Max. SHGC | Assembly Min. VT/SHGC | Assembly Max. U | Assembly Max. SHGC | Assembly Min. VT/SHGC | Assembly Max. U | Assembly Max. SHGC |  | Assembly Min. VT/SHGC |
| Vertical Fenestration, 0% to 40% of Wall |  |  |  |  |  |  |  |  |  |  |
| Nonmetal framing, all | 0.28 | 0.36 | 1.10 (for all types) | 0.28 | 0.36 | 1.10 (for all types) | 0.50 | NR (for all types) |  | NR (for all types) |
| Metal framing, fixed, below 95 ftc | 0.30 | 0.36 |  | 0.30 | 0.36 |  | 0.50 |  |  |  |
| Metal framing, fixed, above 95 ftc | 0.36 | 0.36 |  | 0.36 | 0.36 |  | 0.50 |  |  |  |
| Metal framing, operable, below 95 ftc | 0.40 | 0.33 |  | 0.40 | 0.33 |  | 0.65 |  |  |  |
| Metal framing, operable, above 95 ftc | 0.42 | 0.33 |  | 0.42 | 0.33 |  | 0.65 |  |  |  |
| Entrance door | 0.63 | 0.33 |  | 0.63 | 0.33 |  | 0.77 |  |  |  |
| Skylight, 0% to 3% of Roof |  |  |  |  |  |  |  |  |  |  |
| All types | 0.48 | 0.38 | NR | 0.48 | 0.38 | NR | 0.75 | NR |  | NR |

* The following definitions apply: c.i. = continuous insulation (see Section 3.2), ca= cavity insulation, FC = filled cavity (see Section A2.3.2.5), Ls = liner system (see Section A2.3.2.4); NR = no (insulation)requirement.

a. When using the R-value compliance method for metal building roofs, a thermal spacer block is required (see Section A2.3.2).

b. Exception to Section 5.5.3.2 applies for mass walls above grade.

c. Where any portion of the fenestration frame is installed at or above 95feetabove grade, the unit may meet the requirements for above 95 feet

Section 5.5.4.2.1 Vertical Fenestration Area.

Section 5.5.4.2.1 - Revise Section 5.5.4.2.1 to read as follows:

5.5.4.2.1	Vertical Fenestration Area

The total vertical fenestration area shall not be greater than that specified in Table 5.5-4.

Exception to 5.5.4.2.1

Vertical fenestration complying with Section 5.5.4.4.1, Exception 3.

Section 5.5.4.2.2 Maximum Skylight Fenestration Area.

Section 5.5.4.2.2 - Revise Section 5.5.4.2.2 to read as follows:

5.5.4.2.2	Maximum Skylight Fenestration Area

The total skylight area shall not be greater than that specified in Tables 5.5-4.

Exception to 5.5.4.2.2

The total skylight area is permitted to be increased to no greater than 6% of the gross roof area, provided the skylights meet all of the criteria in to Section 5.5.4.4.2, Exception 1 and the total daylight area under skylights is a minimum of half the floor area of the space.

Section 5.5.4.3 Fenestration U-Factor.

Section 5.5.4.3 - Revise Section 5.5.4.3 to read as follows:

5.5.4.3	Fenestration U-Factor

Fenestration shall have a U-factor not greater than that specified in Tables 5.5-4.

Exception to 5.5.4.3

The U-factor for skylights is permitted to be increased to no greater than 0.90 Btu/h·ft2·°F in Climate Zones 0 through 3 and 0.75 Btu/h·ft2·°F in Climate Zones 4 through 8, provided the sky- lights meet all of the criteria in to Section 5.5.4.4.2, Exception 1.

Section 5.5.4.4.1 SHGC of Vertical Fenestration.

Section 5.5.4.4.1 - Revise the first sentence of  Section 5.5.4.4.1 to read as follows:

Vertical fenestration shall have an SHGC not greater than that specified in Table 5.5-4.

Section 5.5.4.4.2 SHGC of Skylights.

Section 5.5.4.4.2 - Revise the first sentence of  Section 5.5.4.4.1 to read as follows:

Skylights shall have an SHGC not greater than that specified in Table 5.5-4.

Section 5.5.4.5 Fenestration Orientation.

Section 5.5.4.5 - Revise Section 5.5.4.5 to read as follows:

5.5.4.5	Fenestration Orientation

The vertical fenestration shall comply with either (a) or (b):

a.	For Climate Zones 0 through 8,

AW ≤ (AT)/4 and AE ≤ (AT)/4

b.	For Climate Zones 0 through 3,

AW × SHGCW ≤ (AT × SHGCC)/4 and

AE × SHGCE ≤ (AT × SHGCC)/4

For Climate Zones 4 through 8,

AW × SHGCW ≤ (AT × SHGCC)/5 and

AE × SHGCE ≤ (AT × SHGCC)/5

where

Aw = west-oriented vertical fenestration area

Ae = east-oriented vertical fenestration area

AT = total vertical fenestration area

SHGCC =  SHGC criteria in Tables 5.5-4 for each climate zone

SHGCE = SHGC for east-oriented fenestration that complies with Section 5.5.4.4.1

SHGCW = SHGC for west-oriented fenestration that complies with Section 5.5.4.4.1

Exceptions to Section 5.5.4.5

1.	Vertical fenestration that complies with Section 5.5.4.4.1, Exception (3).

2.	Buildings with shade on 75% of the east- and west-oriented vertical fenestration areas

from permanent projections, existing buildings, existing permanent infrastructure, or

topography at 9 a.m. and 3 p.m., respectively, on the summer solstice (June 21 in the north- ern hemisphere).

3.	Alterations and additions with no increase in vertical fenestration area.

4.	Buildings where the west-oriented and east-oriented vertical fenestration area (as defined in Section 5.5.4.5) does not exceed 20% of the gross wall area for each of those façades, and SHGC on those facades is no greater than 90% of the criteria in Table 5.5-4.

5.	Buildings in Climate Zone 8.

Section 5.5.4.6 Visible Transmittance/SHGC Ratio.

Section 5.5.4.6 - Revise the first sentence of  Section 5.5.4.6 to read as follows:

Where automatic daylighting controls are required in accordance with Section 9.4.1.1(e) or (f), fenestration shall have a ratio of VT divided by SHGC not less than that specified in Table 5.5-4 for the appropriate fenestration area.

Section 5.5.5 Linear Thermal Bridges and Point Thermal Bridges.

Section 5.5.5 - Revise Section 5.5.5 to read as follows:

5.5.5 Linear Thermal Bridges and Point Thermal Bridges.

Where linear thermal bridges and point thermal bridges occur as described in Sections 5.5.5.1 through 5.5.5.5, they shall

a. comply with the applicable requirements of Sections 5.5.5.1 through 5.5.5.5 or

b. not exceed the mitigated psi-factors and chi-factors in Table A10.1, where the psi-factors and chi-factors for the thermal bridges are determined in accordance with Normative Appendix A, Section A10.

For the purposes of Section 5.5.5, linear elements that are connected to the building structure by a series of point connections shall be permitted to be characterized as linear thermal bridges or as individual point thermal bridges.

Exceptions to 5.5.5:

1. Reserved

2. Semiheated spaces.

3. Clear-field thermal bridges.

4. Thermal bridges in uninsulated assemblies.

5. Linear and point thermal bridges that have a material thermal conductivity less than 3.0 Btu·in/h·ft2·°F.

6. Alterations to existing buildings other than additions.

7. Roofs that project over exterior walls.

Informative Note: For linear thermal bridges and point thermal bridges that fall under the provisions of Section 4.2 and cannot comply prescriptively with the provisions of Sections 5.5.5.1 through 5.5.5.4, projects can use Section 5.5.5.5, Normative Appendix C, or Normative Appendix G.

Section 5.5.5.1.1 Roof Edges.

Section 5.5.5.1.1 - Revise Section 5.5.5.1.1 to read as follows:

5.5.5.1.1 Roof Edges.

At roof edges without parapets or overhangs, the roof insulation and the wall insulation shall comply with the following, as applicable to the location of the insulation:

a. Where a wall has exterior continuous insulation, the roof insulation shall extend to the exterior of the wall insulation and the wall insulation shall extend to the roof insulation.

b. Where a wall has cavity or integral insulation that represents more than 50% of the total wall insulation R-value, the roof-to-wall insulation shall comply with one of the following:

1. The cavity or integral insulation shall extend to the underside of the roof insulation.

2. The cavity or integral insulation shall extend to the underside of the roof deck, and the roof insulation shall extend to the exterior face of the wall. The wall insulation shall be permitted to be interrupted by roof framing members.

3. Additional insulation having a rated R-value of insulation not less than R-5 shall extend inward on the underside of the roof deck for not less than 2 ft and be permitted to be interrupted by roof framing members.

4. Insulation having a rated R-value of insulation not less than R-5 shall be placed at the exterior of the roof edge and be located between the bottom plane of the roof insulation and the plane of the bottom of the roof deck.

5. The wall insulation values in Tables 5.5-4 shall be adjusted in accordance with Table 5.5.5.1.1-1.6. The roof insulation values in Tables 5.5-4 shall be adjusted in accordance with Table 5.5.5.1.1-2.

c. Where a mass wall has interior insulation that represents more than 50% of the total wall insulation R- value, the interior insulation shall extend to the underside of the roof deck, shall be permitted to be interrupted by framing members, and shall comply with one of the following:

1. Additional insulation having a rated R-value of insulation not less than R-5 shall extend inward on the underside of the roof deck for not less than 2 ft and be permitted to be interrupted by roof framing members.

2. Additional insulation having a rated R-value of insulation not less than R-5 shall be placed at the exterior of the roof edge and be located between the bottom plane of the roof insulation and the plane of the bottom of the roof assembly in contact with the exterior wall.

3. The wall insulation values in Tables 5.5-4 shall be adjusted in accordance with Table 5.5.5.1.1-1.

4. The roof insulation values in Tables 5.5-4 shall be adjusted in accordance with Table 5.5.5.1.1-2.

Informative Note: See Informative Appendix K, Figure K-1.

Section 5.5.5.1.2 Parapets.

Section 5.5.5.1.2 - Revise Section 5.5.5.1.2 to read as follows:

5.5.5.1.2 Parapets.

At roof edges with parapets, the exterior wall insulation shall comply with one or more of the following as applicable to the location of the insulation and wall assembly:

a. Where a wall has exterior continuous insulation, such insulation shall be applied to both vertical sides of the parapet.

Informative Note: See Informative Appendix K, Figure K-2(a).

b. Where a wall has cavity or integral insulation that represents more than 50% of the total wall insulation R-value, the roof to wall intersections at parapets shall comply with one of the following:

1. The wall insulation shall extend within the cavity of the parapet not less than the height of the top of the roof insulation. The wall insulation shall be permitted to be interrupted by roof framing members.

2. Additional insulation having a rated R-value of insulation not less than R-5 shall extend inward on the underside of the roof deck for not less than 2 ft and be permitted to be interrupted by roof framing members.

3. Insulation having a rated R-value of insulation not less than R-5 shall be placed at the exterior of the roof edge and be located between the bottom plane of the roof insulation and the plane of the bottom of the roof deck.

4. The wall insulation values in Table 5.5-4 shall be adjusted in accordance with Table 5.5.5.1.1-1.

5. The roof insulation values in Table 5.5-4 shall be adjusted in accordance with Table 5.5.5.1.1-2.

Informative Note: See Informative Appendix K, Figure K-2(b).

c. Where a mass wall has interior insulation that represents more than 50% of the total wall insulation R- value, the interior insulation shall extend to the underside of the roof deck, shall be permitted to be interrupted by framing members, and shall comply with one of the following:

1. Additional insulation having a rated R-value of insulation not less than R-5 shall extend inward on the underside of the roof deck for not less than 2 ft and be permitted to be interrupted by roof framing members.

2. Additional insulation having a rated R-value of insulation not less than R-5 shall be placed at the exterior of the roof edge and be located between the bottom plane of the roof insulation and the plane of the bottom of the roof assembly in contact with the exterior wall.

3. The wall insulation values in Table 5.5-4 shall be adjusted in accordance with Table 5.5.5.1.1-1.

4. The roof insulation values in Table 5.5-4 shall be adjusted in accordance with Table 5.5.5.1.1-2.

Informative Note: See Informative Appendix K, Figures K-2(c) and K-2(d).

Section 5.5.5.2.1.

Section 5.5.5.2.1- Revise Section 5.5.5.2.1 to read as follows:

5.5.5.2.1

Intermediate floor edges that do not serve as balconies or floor overhangs shall comply with the following as applicable:

a. Where a wall has exterior continuous insulation, such insulation shall extend continuously past the floor edge.

b. Where a wall has cavity insulation that represents more than 50% of the total wall insulation R-value, the cavity insulation shall extend to the underside of the floor deck and shall be permitted to be interrupted by floor framing members and wall top and bottom plates or tracks. (Informative Note: See Informative Appendix K, Figures K-4[a] and K-4[b].)

c. Where a mass wall has integral insulation that represents more than 50% of the total wall insulation R- value, the intermediate floor intersection shall comply with one of the following:

1. The full thickness of integral insulation shall extend past the floor edge.

2. Where the intermediate floor deck extends through the integral insulation, insulation having a rated R-value of insulation not less than R-5 shall be maintained to the full depth of the floor edge on the exterior side of the floor edge.

See Informative Appendix K, Figures K-4(c) and K-4(d).

d. Where a mass wall has interior insulation that represents more than 50% of the total wall insulation R- value, the interior insulation shall extend to the underside of the floor deck, shall be permitted to be interrupted by framing members, and shall comply with one of the following:

1. Additional interior insulation having a rated R-value of insulation not less than R-5 shall cover the full depth of the floor edge. Such insulation shall be permitted to be interrupted by floor framing members. Fire safing applied to the full depth of the floor edge meets this requirement.

2. Additional insulation having a rated R-value of insulation not less than R-5 shall cover the full depth of the floor edge on the exterior side of the wall.

3. The wall insulation values in Table 5.5-4 shall be adjusted in accordance with Table 5.5.5.2.1.

Informative Note: See Informative Appendix K, Figures K-4(e) and K-4(f).

e. Where mass walls have not less than 50% of the rated R-value of insulation on the exterior side of the wall and the remainder on the interior side, the insulation on the interior side of the wall shall be permitted to be interrupted by an intermediate floor. (Informative Note: See Informative Appendix K, Figure K-4[g].)

Section 5.7.2 Permit Application Documentation.

Section 5.7.2- Revise item “c” from Section 5.7.2 to read as follows:

c. Identify air leakage compliance. Continuous air barrier compliance with whole-building pressurization testing in accordance with Section 5.4.3.1.4 shall be clearly indicated on the construction documents.

Section 5.7.3.1 Permit Application Documentation.

Section 5.7.3.1- Revise Section 5.7.3.1 to read as follows:

5.7.3.1 Record Documents. Construction documents shall require that, within 90 days after the date of building envelope acceptance, record documents be provided to the building owner or the designated representative of the building owner. For new buildings or additions that are 10,000 square feet and greater, these documents will be required prior to passing final inspection.  Record documents shall include, as a minimum, those items listed in Section 5.7.2, and the following:

a. A report complying with Section 4.2.5.1.2 providing the results of continuous air barrier compliance with whole-building pressurization testing in accordance with Section 5.4.3.1.4 and verification of the building envelope in accordance with Section 5.9.1.2.

b. Insulation documentation in accordance with Section 5.8.1.11.

c. Field inspections reports of project construction showing compliance with continuous air barrier requirements including proper material handling and storage, use of approved materials and material substitutes, proper material and surface preparation, and air barrier continuity. Air barrier continuity shall be determined by testing or inspecting each type of unique air barrier joint or seam in the building envelope for continuity and defects.

Section 5.8.2.2 Labeling of Fenestration and Door Products.

Section 5.8.2.2 - Revise Section 5.8.2.2 to read as follows:

5.8.2.2 Labeling of Fenestration and Door Products.

All manufactured and site-built fenestration and door products shall demonstrate compliance with U-value and SHGC requirements through a 3rd party labeling program recognized by ANSI, ILACor MiRA and acceptable to the commissioner , or a signed and dated certificate showing compliance through modeling performed using Lawrence Berkley National Labs WINDOW/THERM software at the sizes and Boundary conditions prescribed in NFRC -100/200. The simulation shall be provided by a third-party recognized by ANSI, ILAC,MiRa or an NFRC certified simulator. Air infiltration rate shall be demonstrated by testing to ASTM E283, the test shall be conducted at an independent third-party laboratory recognized by ANSI, ILAC or MiRa, and shall be less than 5 years old.

Section 6 - Heating, Ventilating, and Air Conditioning.

Section 6.1.4.1.1.

Section 6.1.4.1.1 – Add new Section 6.1.4.1.1 to read as follows:

6.1.4.1.1 Where controls are altered for more than 50% of the terminal distribution elements of a space heating or cooling system, the controls for all commonly served terminals and the associated, immediately upstream equipment shall comply with the controls requirements of sections 6.4 and 6.5 as new. Controls for HVAC zones that are altered based on reconfiguration of the associated space notwithstanding alterations to the HVAC system shall comply with sections 6.4 and 6.5.

Exceptions:

1. Controls for terminals located in a space occupied by a different tenant than the altered space.

2. Control provisions of sections 6.4 and 6.5 which are impossible to achieve without an alteration of otherwise unaltered non-control elements of the associated plant equipment.

3. Alterations of controls limited to relocation of control devices within a HVAC zone where there is no reconfiguration of space.

Section 6.1.4.2.

Section 6.1.4.2- Revise Section 6.1.4.2  to read as follows:

6.1.4.2

New cooling systems installed to serve previously uncooled spaces and new heating systems installed to serve previously unheated spaces shall comply with this section as described in Section 6.2.

Section 6.3.2	Criteria.

Section 6.3.2- Revise Item “e” from Section 6.3.2to read as follows:

e.	Heating (if any) shall be provided by a unitary packaged or split-system heat pump that meets the applicable efficiency requirements shown in Table 6.8.1-2 (heat pumps) or Table 6.8.1-4 (packaged terminal and room air conditioners and heat pumps), a fuel- fired furnace that meets the applicable efficiency requirements shown in Table 6.8.1-5 (furnaces, duct furnaces, and unit heaters), , or a baseboard system connected to a boiler that meets the applicable efficiency requirements shown in Table 6.8.1-6 (boilers) and Section 6.4.1.6 (Buildings With High Efficiency Space Heating Gas Boiler Systems). Heating equipment shall also comply with Section 6.4.14.

Revise Item “h” from Section 6.3.2 to read as follows:

h.	If a heat pump equipped with auxiliary internal electric resistance heaters is installed, controls shall be provided that prevent supplemental heater operation when the heat- ing load can be met by the heat pump alone during both steady-state operation and setback recovery. Supplemental heater operation is permitted during outdoor coil defrost cycles. The heat pump must be controlled by either (1) a digital or electronic thermostat designed for heat pump use that energizes auxiliary heat only when the heat pump has insufficient capacity to maintain set point or to warm up the space at a sufficient rate or (2) a multistage space thermostat and an outdoor air thermostat wired to energize auxiliary heat only on the last stage of the space thermostat and when outdoor air temperature is less than 17 °F.

Exception to 6.3.2(h)

Heat pumps that comply with the following:

1. Have a minimum efficiency regulated by NAECA.

2. Meet the requirements in Table 6.8.1-2.

3. Include all usage of internal electric resistance heating.

Section 6.4.1.6 Buildings With High Efficiency Space Heating Gas Boiler Systems.

Section 6.4.1.6 - Add new Section 6.4.1.6 to read as follows:

6.4.1.6 Buildings With High Efficiency Space Heating Gas Boiler Systems

New buildings where space heating is served by one or more gas hot water boilers with a minimum thermal efficiency (Et) of 90% when rated in accordance with the test procedures in Table 6.5.4.1 shall comply with this section, unless otherwise approved by the authority having jurisdiction. The hot water distribution system shall be designed so that the coils and other heat exchangers are selected such that at outdoor design conditions, the hot water return temperature entering the boilers is120°F, or less when the boiler is firing.

Section 6.4.4.1.3	Piping Insulation.

Section 6.4.4.1.3- Remove exception 3 from Section 6.4.4.1.3.

Section 6.5.6.1.2 Spaces Other than Nontransient Dwelling Units.

Section 6.5.6.1.2 - Revise  Section 6.5.6.1.2 to read as follows:

6.5.6.1.2	Spaces Other than Nontransient Dwelling Units

Each fan system serving spaces other than nontransient dwelling units shall have a energy recovery system where the design supply fan airflow rate exceeds the value listed in Tables 6.5.6.1.2-1 and 6.5.6.1.2-2, based on the climate zone and percentage of outdoor air at design airflow conditions. Table 6.5.6.1.2-1 shall be used for all ventilation systems that operate less than 8000 hours per year, and Table 6.5.6.1.2-1 shall be used for all ventilation systems that operate 8000 or more hours per year.

Exceptions to 6.5.6.1.2

1.	Laboratory systems meeting Section 6.5.7.3.

2.	Systems serving spaces that are not cooled and that are heated to less than 60°F.

3.	Heating energy recovery where more than 60% of the outdoor air heating energy is pro- vided from site-recovered energy or on- site- energy in Climate Zones 5 and 6.

4.	 (Reserved)

5.	 (Reserved)

6.	Where the sum of the airflow rates exhausted and relieved within 20 ft of each other is less than 75% of the design ventilation outdoor airflow rate, excluding exhaust air that is any of the following:

a.	used for another energy recovery system,

b.	not allowed by ASHRAE/ASHE Standard 170 for use in energy recovery systems with leakage potential, or

c.	prohibited by the New York City Mechanical Code, or

d.	of Class 4 as defined in ASHRAE Standard 62.1.

7.	Systems in Climate Zone 4 requiring dehumidification during heating mode that employ energy recovery and have a minimum SERR of 0.40.

8.	Systems expected to operate less than 20 hours per week at the outdoor air percentage covered by Table 6.5.6.1.2-1.

9.	Indoor pool dehumidifiers meeting Section 6.5.6.4.

Section 6.6.2.2 Criteria.

Section 6.6.2.2 -Revise  Section 6.6.2.2 to read as follows:

Section 6.7.3.4 System Balancing.

Section 6.7.3.4 - Delete Section 6.7.3.3, Section 6.7.3.3.1, Section 6.7.3.3.2, Section 6.7.3.3.3 and add new Section 6.7.3.3, Section 6.7.3.3.1, Section 6.7.3.4, Section 6.7.3.4.1, Section 6.7.3.4.2, Section 6.7.3.4.3, Section 6.7.3.5, Section 6.7.3.5.1, Section 6.7.3.5.2, Section 6.7.3.5.3, Section 6.7.3.5.4, Section 6.7.3.5.4.1, Section 6.7.3.5.4.2, Section 6.7.3.5.5, Section 6.7.3.5.5.1, Section 6.7.3.5.5.2, Section 6.7.3.5.5.3, and Section 6.7.3.5.5.4 in their entirety.

6.7.3.3 Mechanical, renewable energy, and service water heating systems commissioning and completion requirements.

Prior to passing the final mechanical and plumbing inspections, the approved agency shall provide evidence of mechanical systems commissioning and completion in accordance with the provisions of this section.

Construction document notes shall clearly indicate provisions for commissioning and completion requirements in accordance with this section and are permitted to refer to specifications for further requirements. Copies of all documentation shall be given to the owner or owner’s authorized agent and made available to the building official upon request in accordance with Sections 6.7.3.5.4 and 6.7.3.5.5.

Mechanical systems, renewable energy, and service water heating systems shall include but are not limited to, at a minimum, the following heating, ventilating, air conditioning, service water heating, indoor air quality and refrigeration systems (mechanical and/or passive) and associated controls:

a.	Heating, cooling, air handling and distribution, ventilation, and exhaust systems, and their related air quality monitoring systems.

b.	Air, water, and other energy recovery systems..

c.	Manual or automatic controls, whether local or remote, on energy using systems including but not limited to temperature controls, setback sequences, and occupancy based control, including energy management functions of the building management system.

d.	Plumbing, including insulation of piping and associated valves, domestic and process water pumping, and mixing systems.

e.	Mechanical heating systems and service water heating systems.

f.	Refrigeration systems

g.	Renewable energy and energy storage systems.

h.   Other systems, equipment and components that are used for heating, cooling or ventilation and that affect energy use.

Exceptions to 6.7.3.3

1.	Mechanical systems and service hot water systems in new buildings, additions, or alterations where either the total mechanical equipment capacity being installed or the total mechanical equipment connected load serving the alteration space is less than 480,000 Btu/h (140.7 kW) cooling capacity and 600,000 Btu/h (175.8 kW) combined service water-heating and space-heating capacity.

2.	Renewable energy systems being installed with a generating capacity of less than 25kW.

6.7.3.3.1 Commissioning Plan

A commissioning plan shall be developed by an approved agency and shall include the following items:

a.	A narrative description of the activities that will be accomplished during each phase of commissioning, including the personnel intended to accomplish each of the activities.

b.	A listing of the specific equipment, appliances or systems to be tested, their full sequences of operation, and a description of the tests to be performed, including prerequisite activities and reference to specific checklists or worksheets which are necessary or required by the department.

c.	Functions to be tested including, but not limited to, calibrations and economizer controls.

d.	Conditions under which the test will be performed. Testing shall affirm winter and summer design conditions and full outside air conditions.

e.	Measurable criteria for performance.

6.7.3.4 System Balancing

6.7.3.4.1 Systems Adjusting and Balancing

HVAC systems be balanced in accordance with ASHRAE 111, “Testing, Adjusting, and Balancing of Building HVAC Systems” or other accepted engineering standards as approved by the department. Air and water flow rates shall be measured and adjusted to deliver final flow rates within the tolerances provided in the product specifications. Test and balance activities shall include air system and hydronic system balancing.

6.7.3.4.2	Air Systems Balancing

Each supply air outlet and zone terminal device shall be equipped with means for air balancing in accordance with the requirements of Chapter 6 of the New York City Mechanical Code. Discharge dampers used for air-system balancing are prohibited on constant-volume fans and variable-volume fans with motors 10 hp and larger. Air systems shall be balanced in a manner to first minimize throttling losses then, for fans with system power of greater than 1 hp, fan speed shall be adjusted to meet design flow conditions.

6.7.3.4.3Hydronic Systems Balancing

Individual hydronic heating and cooling coils shall be equipped with means for balancing and measuring flow. Hydronic systems shall be proportionately balanced in a manner to first minimize throttling losses, then the pump impeller shall be trimmed or pump speed shall be adjusted to meet design flow conditions. Each hydronic system shall have either the capability to measure pressure across the pump, or test ports at each side of each pump.

Exceptions to 6.7.3.3.3

The following equipment is not required to be equipped with a means for balancing or measuring flow:

a.	Pumps with pump motors of 5 hp or less.

b.	Where throttling results in no greater than 5 % of the nameplate horsepower draw above that required if the impeller were trimmed.

6.7.3.5 Functional Performance Testing

Functional performance testing specified in Sections 6.7.3.5.1 through 6.7.3.5.3 shall be conducted.

6.7.3.5.1 Equipment

Equipment functional performance testing shall demonstrate the installation and operation of components, systems, and system-to-system interfacing relationships in accordance with approved plans and specifications such that operation, function, and maintenance serviceability for each of the commissioned systems is confirmed. Testing shall include all modes and sequence of operation, including under full-load, part-load and the following emergency conditions:

a.	All modes as described in the sequence of operation.

b.	Redundant or automatic back-up mode.

c.	Performance of alarms.

d.	Mode of operation upon a loss of power and restoration of power.

Exception to 6.7.3.5.1

Unitary or packaged HVAC equipment listed in Tables 6.8.1-1, 6.8.1-2, or 6.8.1-4 that do not require supply air economizers shall only be required to demonstrate functioning under full-load and part-load conditions.

6.7.3.5.2 Controls

HVAC and service water-heating control systems shall be tested to document that control devices, components, equipment and systems are calibrated and adjusted and operate in accordance with approved plans and specifications. Sequences of operation shall be functionally tested to document they operate in accordance with approved plans and specifications.

6.7.3.5.3 Economizers

Air economizers shall undergo a functional test to determine that they operate in accordance with manufacturer’s specifications.

6.7.3.5.4 Preliminary Commissioning Report

A preliminary report of commissioning test procedures and results shall be completed and certified by the approved agency and provided to the building owner or owner’s authorized agent. The report shall be organized with mechanical and service hot water findings in separate sections to allow independent review. The report shall be identified as “Preliminary Commissioning Report” and shall include the completed Commissioning Compliance Checklist, and shall identify:

a.	Itemization of deficiencies found during testing required by this section that have not been corrected at the time of report preparation.

b.	Deferred tests that cannot be performed at the time of report preparation because of climatic conditions.

c.	Climatic conditions required for performance of the deferred tests.

d.	Results of functional performance tests.

e.	Functional performance test procedures used during the commissioning process, including measurable criteria for test acceptance.

6.7.3.5.4.1 Acceptance of Report

Buildings, or portions thereof, shall not be considered acceptable for a final inspection pursuant to Article 116 of Chapter 1 of Title 28 of the Administrative Code until the building official has received a letter of transmittal from the building owner acknowledging that the building owner or owner’s authorized agent has received the Preliminary Commissioning Report.

6.7. 3.5.4.2 Copy of Report

The building official shall be permitted to require that a copy of the Preliminary Commissioning Report be made available for review by the building official.

6.7.3.5.5 Documentation Requirements

The construction documents shall specify that the documents described in Sections 6.7.3.5.5.1 through 6.7.2.3.5.3 be provided to the building owner or owner’s authorized agent within 90 days of the date of receipt of the certificate of occupancy. The construction documents shall also specify that the Final Commissioning Report be provided to the building owner or owner’s authorized agent in accordance with the requirements of Section 6.7.3.5.5.4.

6.7.3.5.5.1 Drawings

Construction documents shall include the location and performance data on each piece of equipment.

6.7.3.5.5.2 Manuals

An operating and maintenance manual shall be provided and include all of the following:

a.	Submittal data stating equipment size and selected options for each piece of equipment requiring maintenance.

b.	Manufacturer’s operation manuals and maintenance manuals for each piece of equipment requiring maintenance, except equipment not furnished as part of the project. Required routine maintenance actions shall be clearly identified.

c.	Name and address of at least one service agency.

d.	HVAC and service hot water controls system maintenance and calibration information, including wiring diagrams, schematics and control sequence descriptions. Desired or field-determined set points shall be permanently recorded on control drawings at control devices or, for digital control systems, in system programming instructions.

6.7.3.5.5.3 System Balancing Report

A written report describing the activities and measurements completed in accordance with Section 6.7.2.3.2.

6.7.3.5.5.4 Final Commissioning Report

Within 30 months for new buildings 500,000 gross square feet or greater, excluding R-2 occupancies, or within 18 months for R-2 occupancies and all other buildings, of the issuance of the certificate of occupancy or letter of completion, an approved agency shall prepare a report of test procedures and results, including test procedures and results performed after occupancy, identified as the “Final Commissioning Report”, provide such report to the building owner, and submit a certification to the department with applicable fees in accordance with department rules. The owner of a building 500,000 gross square feet or greater may apply for an extension of time to the building official based on good cause, in accordance with department rules. Such report shall include the following:

a.	Results of functional performance tests.

b.	Disposition of deficiencies found during testing, including details of corrective measures used or proposed.

c.	Functional performance test procedures used during the commissioning process including measurable criteria for test acceptance, provided herein for repeatability.

Exception to 6.7.3.5.5.4

Deferred tests that cannot be performed at the time of report preparation due to climatic conditions.

Section 7 - Service Water Heating.

Section 7.2.1	Requirements for All Compliance Paths.

Section 7.2.1- Revise Section 7.2.1 to read as follows:

7.2.1	Requirements for All Compliance Paths

Service water heating systems and equipment shall comply with Sections 7.1, “General”; 7.4, “Mandatory Provisions”; 7.7, “Submittals”; Section 6.7.3.3, “Mechanical, renewable energy, and service water heating systems commissioning and completion requirements”; and 7.8, “Product Information.”

Section 7.4.7 Demand responsive water heating.

Section 7.4.7 – Add new Section 7.4.7 to read as follows:

7.4.7 Demand responsive water heating.

Electric storage water heaters with a rated water storage volume of 40 gallons (150L) to 120 gallons (450L) and a nameplate input rating equal to or less than 12kW shall be provided with demand responsive controls in accordance with Table 7.4-3.

Exceptions:

1.	Water heaters that provide a hot water delivery temperature of 180°F (82°C) or greater.

2.	Water heaters that comply with Section IV, Part HLW or Section X of the ASME Boiler and Pressure Vessel Code.

3.	Water heaters that use 3-phase electric power.

Table 7.4-3 Demand Responsive Controls for Water Heating.

Table 7.4-3 – Add new Table 7.4-3 to read as follows:

Table 7.4-3 Demand Responsive Controls for Water Heating

| Equipment Type | Controls |  |
| --- | --- | --- |
|  | Manufactured before 7/1/2025 | Manufactured on or after 7/1/2025 |
| Electric storage Water heaters | AHRI Standard 1430 or ANSI/CTA-2045-B Level 1 and also capable of initiating water heating to meet the temperature set point in response to a demand response signal. | AHRI Standard 1430 |

Section 8 - Power.

Section 8.4.3.1 Monitoring.

Section 8.4.3.1 – Revise Section 8.4.3.1 to read as follows:

8.4.3.1	Monitoring

Measurement devices shall be installed in new buildings to monitor the electrical energy use for each of the following separately:

a.	Total electrical energy

b.	HVAC systems

c.	Interior lighting

d.	Exterior lighting

e.	Receptacle circuits

f.  Refrigeration systems

g. Electric vehicle charging

For buildings with tenants, these systems shall be separately monitored for the total build- ing and (excluding shared systems) for each individual tenant.

Exception to 8.4.3.1

Where the design load for each of any of the categories (b) through (f) are less than 10% of the whole-building load, these categories shall be allowed to be loads combined with other categories.

Section 8.4.3.2 Recording and Reporting.

Section 8.4.3.2 – Revise the exceptions from Section 8.4.3.2 to read as follows:

Exceptions to Sections 8.4.3.1 and 8.4.3.2

1.	Building less than 10,000 ft2.

2.	Individual tenant spaces less than 5,000 ft2.

3.	Dwelling units.

4.	Residential buildings with less than 10,000 ft2 of common area.

5.	Critical equipment and life-safety branches of NFPA 70 Article 517.

Section 8.4.5 Electrification Ready

Section 8.4.5 – Delete  Section 8.4.5 .

Section 8.4.5 Measurement of electrical consumption of tenant spaces in covered buildings.

Section 8.4.5 – Add new  Section 8.4.5 to read as follows:

8.4.5 Measurement of electrical consumption of tenant spaces in covered buildings

Each covered tenant space in a new building shall be equipped with a separate meter or sub-meter to measure the electrical consumption of such space when let or sublet. The terms covered building, meter, sub-meter, tenant space and covered tenant space shall have the same meanings as defined in Section 28-311.2 of the NYC Administrative Code.

Section 8.4.6  Dwelling unit metering.

Section 8.4.6 – Add new  Section 8.4.6 to read as follows:

8.4.6 Dwelling unit metering.

Each dwelling unit located in a Group R-2 building shall have a separate electrical meter.

Section 9 - Lighting.

Section 9.4.1.1 Interior Lighting Controls.

Section 9.4.1.1 – Revise item “g” from  Section 9.4.1.1   to read as follows:

g.	Automatic reduction control (full OFF complies): The general lighting power in the space shall be automatically reduced by at least 50% within 15 minutes of all occupants leaving the space. The controls in open plan offices, cafeteria dining areas, and fast food dining areas, 300 ft2 and greater in area, shall be configured so that general lighting power in each control zone is reduced by not less than 80% of the full zone general lighting power in a reasonably uniform illumination pattern within 15 minutes of all occupants leaving that control zone. Control functions that switch control zone lights completely off when the zone is vacant meet this requirement.

In offices greater than300 ft2, control zones for general lighting shall

1. be limited to 600 ft2 and

2. automatically reduce general lighting by at least 80% of full power within 15 minutes of all occupants leaving a control zone.

Section 9.4.1.1 – Revise item “h” from  Section 9.4.1.1   to read as follows:

h.	Automatic full OFF control: All lighting in the space, including lighting connected to emergency circuits, shall be automatically shut off within 15  minutes of all occupants leaving the space. A control device meeting this requirement shall control no more than 5000 ft2 , provided that for open plan office spaces or dining spaces a control device meeting this requirement shall control not greater than 600 ft2.

Exception to 9.4.1.1(h)

The following lighting is not required to be automatically shut off:

1.  Lighting required for 24/7 operation.

2. Lighting in spaces where patient care is rendered.

3. 	General lighting and task lighting in spaces where automatic shutoff would endanger the safety or security of the room or building occupants.

4.	Lighting load exceeding 0.02 W/ft2 multiplied by the gross lighted floor area of the building.

Section 9.4.1.5 Demand responsive lighting controls.

Section 9.4.1.5 – Add new  Section 9.4.1.5 to read as follows:

9.4.1.5 Demand responsive lighting controls. Interior general lighting in Group B, E, M, and S occupancies shall have demand responsive controls complying with Section 9.4.1.5.1 in not less than 75 percent of the interior floor area.

Exceptions:

- Where the combined interior floor area of Group B, E, M, and S occupancies is less than 10,000 square feet.

- Buildings where a demand response signal is not available from a controlling entity other than the owner.

- Parking garages.

- Ambulatory care facilities.

- Outpatient clinics.

- Physician or dental offices.

Section 9.4.1.5.1 Demand responsive lighting controls function.

Section 9.4.1.5.1 – Add new  Section 9.4.1.5.1 to read as follows:

9.4.1.5.1 Demand responsive lighting controls function. Demand responsive controls for lighting shall be capable of the following:

- Automatically reducing the output of controlled lighting to 80 percent or less of full power or light output upon receipt of a demand response signal.

- Where high-end trim has been set, automatically reducing the output of controlled lighting to 80 percent or less of the high-end trim setpoint upon receipt of a demand response signal.

- Dimming controlled lights gradually and continuously over a period of not longer than 15 minutes to achieve their demand response setpoint.

- Returning controlled lighting to its normal operational settings at the end of the demand response period.

Exception: Storage rooms and warehouse storage areas shall be permitted to switch off  25  percent or more of general lighting power rather than dimming.

Section 9.4.3.1 Lamp and Luminaire Efficacy.

Section 9.4.3.1 – Revise  Section 9.4.3.1 to read as follows:

9.4.3.1 Lamp and Luminaire Efficacy.

At least 90% of the permanently installed luminaires shall use lamps with an efficacy of at least  75  lm/W or have a total luminaire efficacy of at least  50 lm/W.

Section 9.4.4 Horticultural Lighting.

Section 9.4.4 – Delete Section 9.4.4, Section  9.4.4.1 and 9.4.4.2 and add new Section 9.4.4   to read as follows:

9.4.4 Horticultural Lighting.

Luminaires in indoor grow spaces and greenhouse buildings used for horticultural lighting shall have a photosynthetic photon efficacy (PPE) of at least 2.1 μmol/J. Horticultural lighting in greenhouse spaces and indoor grow spaces shall be controlled by a device that automatically turns off the horticultural lighting at specific programmed times.

Table 9.5.1 Lighting Power Density Allowances Using the Building Area Method.

Table 9.5.1 – Delete Table 9.5.1and add new Table 9.5.1 to read as follows:

Table 9.5.1 Lighting Power Density Allowances Using the

Building Area Method

| Building Area Typea | LPD, W/ft2 |
| --- | --- |
| Automotive facility | 0.64 |
| Convention center | 0.64 |
| Courthouse | 0.74 |
| Dining: Bar lounge/leisure | 0.69 |
| Dining: Cafeteria/fast food | 0.66 |
| Dining: Family | 0.61 |
| Dormitory | 0.52 |
| Exercise center | 0.65 |
| Fire station | 0.50 |
| Gymnasium | 0.67 |
| Health-care clinic | 0.68 |
| Hospital | 0.86 |
| Hotel/motel | 0.53 |
| Library | 0.78 |
| Manufacturing facility | 0.60 |
| Motion picture theater | 0.43 |
| Multifamily | 0.46 |
| Museum | 0.56 |
| Office | 0.62 |
| Parking garage | 0.12 |
| Penitentiary | 0.65 |
| Performing arts theater | 0.82 |
| Police station | 0.62 |
| Post office | 0.62 |
| Religious facility | 0.66 |
| Retail | 0.78 |
| School/university | 0.67 |
| Sports arena | 0.73 |
| Town hall | 0.67 |
| Transportation | 0.51 |
| Warehouse | 0.41 |
| Workshop | 0.83 |

a. In cases where both a general building area type and a specific building area type are listed, the specific building area type shall apply.

b.	Neither the area of the dwelling units nor the wattage of lighting in the dwelling units is counted

Section 9.5.2.1 Space-by-Space Method of Calculating Interior Lighting Power Allowance.

Section 9.5.2.1 – Revise Item “c”  from Section 9.5.2.1 to read as follows:

c. Based on the space type selected for each space or subspace, determine the lighting power allowance of each space or subspace by multiplying the calculated area of the space or subspace by the appropriate LPD allowance determined in Section 9.6.1(a). For space types not listed, selection of a reasonable equivalent category shall be permitted. Where a building has unfinished spaces, the lighting power allowance for the unfinished spaces shall be the total connected lighting power for those spaces, or 0.2 watts per square foot, whichever is less.

Table 9.5.2.1-1 Space-by-Space Lighting Power Density Allowances and Minimum Control Requirements Using Either Method.

Table 9.5.2.1-1 – Revise Table 9.5.2.1-1 to read as follows:

Table 9.5.2.1-1 Space-by-Space Lighting Power Density Allowances and Minimum Control Requirements Using Either Method

| Informative Note: This table is divided into two sections; this first section covers space types that can be commonly found in multiple building types. The second part of this table covers space types that are typically found in a single building type. |  |  |  | The control functions below shall be implemented in accordance with the descriptions found in the referenced paragraphs within Section 9.4.1.1. For each space type: (1) All REQs shall be implemented. (2) At least one ADD1 (when present) shall be implemented. (3) At least one ADD2 (when present) shall be implemented. |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Local Control | Manual ON | Partial ON | Multilevel Lighting Control | Daylight Response Sidelighting | Daylight Response Toplighting | Auto Reduction | Auto Full OFF | Scheduled Shutoff |
| Common Space Types1 | LPD Allowances, W/ft2 |  | RCR Threshold | 9.4.1.1[a] | 9.4.1.1[b] | 9.4.1.1[c] | 9.4.1.1[d] | 9.4.1.1[e] | 9.4.1.1[f] | 9.4.1.1[g] | 9.4.1.1[h]) | 9.4.1.1[i]) |
| Atrium |
| <20 ft in height | 0.32 |  | NA | REQ | ADD1 | ADD1 |  | REQ | REQ |  | ADD2 | ADD2 |
| ≥20 ft and ≤40 ft in height | 0.41 |  | NA | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  | ADD2 | ADD2 |
| >40 ft in height | 0.51 |  | NA 11 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  | ADD2 | ADD2 |
| Audience Seating Area |
| Auditorium | 0.57 |  | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  | ADD2 | ADD2 |
| Gymnasium | 0.23 |  | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  | ADD2 | ADD2 |
| Motion picture theater | 0.27 |  | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  | ADD2 | ADD2 |
| Performing arts theater | 1.10 |  | 8 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  | ADD2 | ADD2 |
| Sports arena | 0.27 |  | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  | ADD2 | ADD2 |
| All other audience seating areas | 0.23 |  | 4 | REQ | ADD1 | ADD1 |  | REQ | REQ |  | ADD2 | ADD2 |
| Banking Activity Area | 0.56 |  | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  | ADD2 | ADD2 |
| Classroom/Lecture Hall/Training Room |  |  |  |  |  |  |  |  |  |  |  |  |
| Shop classroom | 1.17 |  | 6 | REQ | ADD1 | ADD1 |  | REQ | REQ |  |  | REQ |
| All other classrooms/lecture halls/training rooms | 0.72 |  | 4 | REQ | REQ | ADD1 | REQ | REQ | REQ |  | REQ |  |
| Computer Room | 0.75 |  | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  | ADD2 | ADD2 |
| Conference/Meeting/Multipurpose Rooms | 0.88 |  | 6 | REQ | REQ ADD1 | ADD1 | REQ | REQ | REQ |  | REQ |  |
| Control/(Editing Room or Booth) | 0.73 |  | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  | ADD2 | ADD2 |
| Copy/Print Room | 0.5 |  | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  | REQ |  |
| Corridor | 0.44 |  | width 8 ft | REQ |  |  |  | REQ | REQ | REQ | ADD2 | ADD2 |
| Courtroom | 1.06 |  | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  | ADD2 | ADD2 |
| Dining Areas |  |  |  |  |  |  |  |  |  |  |  |  |
| Bar/lounge or leisure dining | 0.62 |  | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  | ADD2 | ADD2 |
| Cafeteria or fast-food dining | 0.36 |  |  | REQ | ADD1 | ADD1 |  | REQ | REQ |  | ADD2 | ADD2 |
| Family dining | 0.52 |  | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  | ADD2 | ADD2 |
| All other dining areas | 0.42 |  | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  | ADD2 | ADD2 |
| Electrical/Mechanical Room7 | 0.39 |  | 6 | REQ |  |  |  | REQ | REQ |  |  |  |
| Emergency Vehicle Garage | 0.41 |  | 4 | REQ | ADD1 | ADD1 |  | REQ | REQ |  | ADD2 | ADD2 |
| Equipment Room | 0.73 |  |  | REQ | ADD1 | ADD1 |  | REQ | REQ |  | ADD2 |  |
| Food Preparation Area | 0.92 |  | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  | ADD2 | ADD2 |
| Guest Room | 0.41 |  | 6 | See Section 9.4.1.3(b). |  |  |  |  |  |  |  |  |
| Laboratory |  |  |  |  |  |  |  |  |  |  |  |  |
| In or as a classroom | 1.04 |  | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ | ADD2 | ADD2 |
| All other laboratories | 1.21 |  | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  | ADD2 | ADD2 |
| Laundry/Washing Area | 0.43 |  | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  | ADD2 REQ | ADD2 |
| Loading Dock, Interior | 0.51 |  | 6 | REQ | ADD1 | ADD1 |  | REQ | REQ |  | ADD2 | ADD2 |
| Lobby |  |  |  |  |  |  |  |  |  |  |  |  |
| Elevator | 0.52 |  | 6 | REQ |  |  |  | REQ | REQ |  | ADD2 | ADD2 |
| Hotel | 0.48 |  | 4 | REQ |  |  |  | REQ | REQ |  | ADD2 | ADD2 |
| Motion picture theater | 0.20 |  | 4 | REQ |  |  |  | REQ | REQ |  | ADD2 | ADD2 |
| Performing arts theater | 0.82 |  | 6 | REQ |  |  |  | REQ | REQ | REQ | ADD2 | ADD2 |
| All other lobbies | 0.80 |  | 4 | REQ |  |  |  | REQ | REQ | REQ | ADD2 | ADD2 |
| Locker Room | 0.43 |  | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  | REQ |  |
| Lounge/Breakroom9, 10 |  |  |  |  |  |  |  |  |  |  |  |  |
| Mother's/wellness room | 0.68 |  | 6 | REQ | ADD1 | ADD1 | REQ |  |  |  | REQ |  |
| All other lounges/breakrooms | 0.44 |  | 4 | REQ | REQ ADD1 | ADD1 | REQ | REQ | REQ |  | REQ |  |
| Office |  |  |  |  |  |  |  |  |  |  |  |  |
| Office≤150 ft2 | 0.73 |  | 8 | REQ | ADD1 | ADD1 | REQ |  |  |  | REQ |  |
| Office >150 and ≤300 ft2 | 0.66 |  | 8 | REQ | ADD1 | ADD1 | REQ |  |  |  | REQ |  |
| Offices >300 ft2 | 0.56 |  | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ | REQ |  |
| Parking Garage |  |  |  |  |  |  |  |  |  |  |  |  |
| Daylight transition ]one | 1.06 |  | 4 |  |  |  | See Section 9.4.1.2. |  |  |  |  |  |
| All other parking and drive areas | 0.11 |  | 4 |  |  |  | See Section 9.4.1.2. |  |  |  |  |  |
| Pharmacy Area | 1.23 |  | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  | ADD2 | ADD2 |
| Restrooms | 0.74 |  | 8 |  | ADD1 | ADD1 |  | REQ | REQ |  | REQ |  |
| Sales Area4 (For accent lighting, see Section 9.5.2.2[b].) | 0.85 |  | 6 | REQ | ADD1 | ADD1 | REQ |  | REQ |  | ADD2 | ADD2 |
| Seating Area, General | 0.21 |  | 4 | REQ | ADD1 | ADD1 |  | REQ | REQ |  | ADD2 | ADD2 |
| Security Screening |  |  |  |  |  |  |  |  |  |  |  |  |
| Airport bus ship train transportation screening | 0.93 |  | 6 | REQ |  |  |  | REQ | REQ |  | ADD2 |  |
| Airport bus ship train transportation screening queue | 0.56 |  | 6 | REQ |  |  |  | REQ | REQ |  | ADD2 |  |
| General security screening | 0.64 |  | 6 | REQ |  |  |  | REQ | REQ |  | ADD2 |  |
| Stairway The space containing the stairway shall determine the LPD and control requirements for the stairway. |  |  |  |  |  |  |  |  |  |  |  |  |
| Stairwell | 0.47 |  | 10 |  |  |  | REQ | REQ | REQ | REQ | ADD2 | ADD2 |
| Storage Room |  |  |  |  |  |  |  |  |  |  |  |  |
| < 50 ft2 | 0.43 |  | 9 | REQ | REQ |  |  |  |  |  | ADD2 | ADD2 |
| ≥ 50 ft2 | 0.35 |  | 6 | REQ | ADD1 | ADD1 |  | REQ | REQ |  | REQ |  |
| Vehicular Maintenance Area | 0.53 |  | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  | ADD2 | ADD2 |
| Workshop (including workshop classrooms) | 1.09 |  | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  | ADD2 | ADD2 |

a. Where both a common space type and a building-specific space type are listed, the building specific space type shall apply (see Table 9.5.2.1-2 for building-specific space types).

b. Automatic daylight responsive controls are mandatory only if the space meets the requirements of the specified sections.

Table 9.5.2.1-2 Space-by-Space Lighting Power Density Allowances and Minimum Control Requirements Using Either Method.

Table 9.5.2.1-2 – Revise Table 9.5.2.1-2 to read as follows:

Table 9.5.2.1-2 Space-by-Space Lighting Power Density Allowances and Minimum Control Requirements Using Either Method

| Informative Note: This table covers building-specific space types typically foundin a single building type. Table 9.5.2.1-1 covers common space types typicallyfound in multiple building types. |  |  |  |  |  |  |  |  |  |  | The control functions below shall be implemented in accordance with the descriptions found within Section 9.4.1.1. For each space type: (1) All REQs shall be implemented. (2) At least one ADD1 (when present) shall be implemented. (3) At least one ADD2 (when present) shall be implemented. |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Local Control |  | Manual ON | Partial Auto ON |  |  | Bilevel Multilevel Lighting Control |  | Daylight Response Sidelighting | Daylight Response Toplighting |  | Auto Reduction |  | Auto Full OFF | Scheduled Shutoff |  |
| Building-Specific Space Typesa | LPD Allowances, W/ft2 | RCR Threshold |  |  | 9.4.1.1[a] |  | 9.4.1.1[b] | 9.4.1.1[c] |  |  | 9.4.1.1[d] |  | 9.4.1.1[e] | 9.4.1.1[f] |  | 9.4.1.1[g] |  | 9.4.1.1[h]) | 9.4.1.1[i]) |  |
| Casino-Gaming Area |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Betting/sportsbook/keno/bingo area | 0.82 |  | 5 |  |  |  |  |  |  | REQ |  |  |  |  |  |  | ADD2 |  |  | ADD2 |
| High-limit game area | 1.68 |  | 4 |  |  |  |  |  |  | REQ |  |  |  |  |  |  | ADD2 |  |  | ADD2 |
| Slot machine/digital gaming area | 0.54 |  | 5 |  |  |  |  |  |  | REQ |  |  |  |  |  |  | ADD2 |  |  | ADD2 |
| Table games area | 1.09 |  | 5 |  |  |  |  |  |  | REQ |  |  |  |  |  |  | ADD2 |  |  | ADD2 |
| Convention Center—Exhibit Space | 0.5 |  | 4 | REQ |  | ADD1 |  |  | ADD1 | REQ |  | REQ |  |  | REQ |  |  |  |  | REQ |
| Correctional Facilities |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Audience seating area | 0.56 |  | 4 | REQ |  | ADD1 |  |  | ADD1 |  |  | REQ |  |  | REQ |  | ADD2 |  |  | ADD2 |
| Classroom/lecture hall/training room | 0.74 |  | 4 | REQ |  | ADD1 |  |  | ADD1 | REQ |  | REQ |  |  | REQ |  |  |  |  |  |
| Confinement cells | 0.6 |  | 6 | REQ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | REQ |
| Dining area | 0.35 |  | 6 | REQ |  | ADD1 |  |  | ADD1 | REQ |  | REQ |  |  | REQ |  | ADD2 |  |  | ADD2 |
| Dormitory—Living Quarters | 0.46 |  | 8 | REQ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Facility for the Visually Impaired3 (A facility for the visually impaired is a facility that can be documented as being designed to comply with the light levels in ANS,/,ES R3-28 and that is or will be licensed by local/state authorities for senior long-term care, adult daycare, senior support, and/or people with special visual needs.) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Chapel (used primarily by residents) | 0.58 |  | 4 | REQ |  | ADD1 |  |  | ADD1 | REQ |  | REQ |  |  | REQ |  | ADD2 |  |  | ADD2 |
| Corridor (used primarily by residents) | 0.71 |  | width 8 ft | REQ |  |  |  |  |  |  |  | REQ |  |  | REQ | REQ | ADD2 |  |  | ADD2 |
| Dining (used primarily by residents) | 1.22 |  | 4 | REQ |  | ADD1 |  |  | ADD1 | REQ |  | REQ |  |  | REQ |  | ADD2 |  |  | ADD2 |
| Lobby | 1.44 |  | 4 | REQ |  |  |  |  |  |  |  | REQ |  |  | REQ | REQ | ADD2 |  |  | ADD2 |
| Recreation room/common living room (used primarily by residents) | 1.2 |  | 6 | REQ |  | ADD1 |  |  | ADD1 | REQ |  | REQ |  |  | REQ |  | ADD2 |  |  | ADD2 |
| Restroom (used primarily by residents) | 0.96 |  | 8 |  |  |  |  |  |  |  |  | REQ |  |  | REQ |  | REQ |  |  |  |
| Fire Station—Sleeping Quarters | 0.19 |  | 6 | REQ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Gymnasium/Fitness Center |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Exercise area | 0.50 |  | 4 | REQ |  | ADD1 |  |  | ADD1 | REQ |  | REQ |  |  | REQ |  | ADD2 |  |  | ADD2 |
| Playing area | 0.75 |  | 4 | REQ |  | ADD1 |  |  | ADD1 | REQ |  | REQ |  |  | REQ |  | ADD2 |  |  | ADD2 |
| Healthcare Facility |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Control room (MRT/CT/radiology/PET) | 0.78 |  | 8 | REQ |  | REQ |  |  |  | REQ |  |  |  |  |  |  | REQ |  |  |  |
| Exam/treatment room | 1.16 |  | 8 | REQ |  |  |  |  |  | REQ |  | REQ |  |  | REQ |  | ADD2 |  |  | ADD2 |
| Hospital corridor | 0.61 |  | width 8 ft | REQ |  |  |  |  |  |  |  | REQ |  |  | REQ | ADD2 | ADD2 |  |  | ADD2 |
| Imaging room | 0.94 |  | 6 | REQ |  |  |  |  |  | REQ |  |  |  |  |  |  | ADD2 |  |  | ADD2 |
| Lounge | 0.77 |  | 6 | REQ |  | ADD1 |  |  | ADD1 | REQ |  | REQ |  |  | REQ |  | REQ |  |  |  |
| Medical supply room | 0.54 |  | 6 | REQ |  | ADD1 |  |  | ADD1 |  |  |  |  |  |  |  | REQ |  |  |  |
| Nursery | 0.87 |  | 6 | REQ |  |  |  |  |  | REQ |  | REQ |  |  | REQ |  | ADD2 |  |  | ADD2 |
| Nurse’s station | 0.75 |  | 6 | REQ |  |  |  |  |  | REQ |  | REQ |  |  | REQ |  | ADD2 |  |  | ADD2 |
| Operating room | 1.87 |  | 6 | REQ |  |  |  |  |  | REQ |  |  |  |  |  |  |  |  |  |  |
| Patient room | 0.45 |  | 6 | REQ |  |  |  |  |  | REQ |  |  |  |  |  |  |  |  |  |  |
| Physical therapy room | 0.82 |  | 6 | REQ |  |  |  |  |  | REQ |  | REQ |  |  | REQ |  | ADD2 |  |  | ADD2 |
| Recovery room | 0.89 |  | 6 | REQ |  |  |  |  |  | REQ |  |  |  |  |  |  | ADD2 |  |  | ADD2 |
| Telemedicine | 1.44 |  | 8 |  |  | ADD1 |  |  | ADD1 | REQ |  | REQ |  |  | REQ |  | REQ |  |  |  |
| Library |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Reading area | 0.77 |  | 4 | REQ |  | ADD1 |  |  | ADD1 | REQ |  | REQ |  |  | REQ |  | ADD2 |  |  | ADD2 |
| Stacks | 1.18 |  | 4 | REQ |  | ADD1 |  |  | ADD1 |  |  |  |  |  |  | REQ | ADD2 |  |  | ADD2 |
| Manufacturing Facility |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Detailed manufacturing area | 0.75 |  | 4 | REQ |  | ADD1 |  |  | ADD1 |  |  | REQ |  |  | REQ |  | ADD2 |  |  | ADD2 |
| Extra-high bay area (>50 ft floor-to-ceiling height) | 0.73 |  | 8 | REQ |  | ADD1 |  |  | ADD1 |  |  | REQ |  |  | REQ |  | ADD2 |  |  | ADD2 |
| High bay area (25 to 50 ft floor-to-ceiling height) | 0.58 |  | 6 | REQ |  | ADD1 |  |  | ADD1 |  |  | REQ |  |  | REQ |  | ADD2 |  |  | ADD2 |
| Low bay area ( 25 ft floor-to-ceiling height) | 0. 5 |  | 3 | REQ |  | ADD1 |  |  | ADD1 |  |  | REQ |  |  | REQ |  | ADD2 |  |  | ADD2 |
| Museum |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| General exhibition area | 0.31 |  | 6 | REQ |  | ADD1 |  |  | ADD1 | REQ |  | REQ |  |  | REQ |  | ADD2 |  |  | ADD2 |
| Restoration room | 0.77 |  | 4 | REQ |  | ADD1 |  |  | ADD1 | REQ |  | REQ |  |  | REQ |  | ADD2 |  |  | ADD2 |
| Performing Arts Theater—Dressing Room | 0.35 |  | 6 | REQ |  | ADD1 |  |  | ADD1 | REQ |  | REQ |  |  | REQ |  | REQ |  |  |  |
| Post Office—Sorting Area | 0. 1 |  | 4 | REQ |  | ADD1 |  |  | ADD1 |  |  | REQ |  |  | REQ | REQ | ADD2 |  |  | ADD2 |
| Religious Facility |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Audience seating area | 0. 2 |  | 4 | REQ |  |  |  |  |  | REQ |  | REQ |  |  | REQ |  | ADD2 |  |  | ADD2 |
| Fellowship hall | 0.5 |  | 4 | REQ |  | ADD1 |  |  | ADD1 | REQ |  | REQ |  |  | REQ |  | ADD2 |  |  | ADD2 |
| Worship/pulpit/choir area | 0. 5 |  | 4 | REQ |  | ADD1 |  |  | ADD1 | REQ |  | REQ |  |  | REQ |  | ADD2 |  |  | ADD2 |
| Retail Facilities |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Dressing/fitting room | 0.45 |  |  | REQ |  | ADD1 |  |  | ADD1 | REQ |  |  |  |  | REQ |  | REQ |  |  | ADD2 |
| Hair care | 0.65 |  | 6 | REQ |  | ADD1 |  |  |  |  |  |  |  |  |  |  | ADD2 |  |  | ADD2 |
| Mall concourse | 0.5 |  | 4 | REQ |  | ADD1 |  |  | ADD1 | REQ |  |  |  |  | REQ |  | ADD2 |  |  | ADD2 |
| Massage | 0. 1 |  |  | REQ |  | ADD1 |  |  | ADD1 | REQ |  |  |  |  |  |  | ADD2 |  |  | ADD2 |
| Nail care | 0. 5 |  | 6 | REQ |  | ADD1 |  |  | ADD1 |  |  |  |  |  |  |  | ADD2 |  |  | ADD2 |
| Sports Arena—Playing Area8 (Class of play as defined by ANSI/IES RP-6) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Class I facility | 2.26 |  | 4 | REQ |  | REQ |  |  |  |  |  | REQ |  |  | REQ |  |  |  |  | REQ |
| Class II facility | 1.45 |  | 4 | REQ |  | REQ |  |  |  |  |  | REQ |  |  | REQ |  |  |  |  | REQ |
| Class III facility | 1.08 |  | 4 | REQ |  | REQ |  |  |  |  |  | REQ |  |  | REQ |  |  |  |  | REQ |
| Class IV facility | 0. 5 |  | 4 | REQ |  | ADD1 |  |  | ADD1 |  |  | REQ |  |  | REQ |  | ADD2 |  |  | ADD2 |

a. Where both a common space type and a building-specific space type are listed, the building specific space type shall apply (see Table 9.5.2.1-1 for common space types).

b. Automatic daylight responsive controls are mandatory only if the space meets the requirements of the specified sections.

Section 9.9.1	Verification and Testing.

Section 9.9.1– Revise Item “b”  from Section 9.9.1to read as follows:

b.	Automatic Time Switches

1.	Confirm that the automatic time-switch control is programmed with accurate weekday, weekend, and holiday (as applicable) schedules.

2.	Document for the owner automatic time-switch control programming, including weekday, weekend, and holiday schedules, as well as all setup and preference program settings.

3.	Verify that correct time and date are properly set in the time switch.

4.	Verify that any battery backup (as applicable) is installed and energized.

5.	Verify that the override time limit is set to no more than two (2) hours.

6.	Simulate occupied condition. Verify and document the following:

1. 	All lights can be turned on and off by their respective area control switch.

2. 	The switch only operates lighting in the enclosed space in which the switch is located.

7.	Simulate unoccupied condition. Verify and document the following:

i All nonexempt lighting turns off.

ii 	Manual override switch allows only the lights in the enclosed space where the override switch is located to turn on or remain on until the next scheduled shut off occurs.

8.  Additional testing as specified by the registered design professional.

Section 9.9.1.1 Documentation Requirements.

Section 9.9.1.1 – Add new Section 9.9.1.1 to read as follows:

9.9.1.1 Documentation Requirements

The construction documents shall specify that the documents described in this section be provided to the building owner or owner’s authorized agent within 90 days of the date of receipt of the certificate of occupancy.

Section 9.9.1.1.1 Drawings.

Section 9.9.1.1.1 – Add new Section 9.9.1.1.1 to read as follows:

9.9.1.1.1 Drawings

Construction documents shall include the location and catalogue number of each piece of equipment.

Section 9.9.1.1.2 Manuals.

Section 9.9.1.1.2 – Add new Section 9.9.1.1.2 to read as follows:

9.9.1.1.2 Manuals

An operating and maintenance manual shall be provided and include the following:

a. Name and address of not less than one service agency for installed equipment.

b. A narrative of how each system is intended to operate, including recommended setpoints.

c. Submittal data indicating all selected options for each piece of lighting equipment and lighting controls.

d. Operation and maintenance manuals for each piece of lighting equipment. Required routine maintenance actions, cleaning and recommended relamping shall be clearly identified.

e. A schedule for inspecting and recalibrating all lighting controls.

Section 9.9.1.1.3 Report.

Section 9.9.1.1.3 – Add new Section 9.9.1.1.3 to read as follows:

9.9.1.1.3 Report

A report of test results shall be provided and include the following:

a. Results of functional performance tests.

b. Disposition of deficiencies found during testing, including details of corrective measures used or proposed.

Section 10- Other Equipment.

Section 10.4.3.5.1 Motor.

Section 10.4.3.5.1 – Add new Section 10.4.3.5.1 to read as follows:

10.4.3.5.1 Motor

Induction motors with a Class IE2 efficiency ratings, as defined by IEC EN 60034-30, or alternative technologies, such as permanent magnet synchronous motors that have equal or better efficiency, shall be used.

Section 10.4.3.5.2 Transmission.

Section 10.4.3.5.2 – Add new Section 10.4.3.5.2 to read as follows:

10.4.3.5.2 Transmission

Transmissions shall not reduce the efficiency of the combined motor/transmission for the Class IE2 motor for elevators with capacities below 4,000 lbs. Gearless machines shall be assumed to have a 100% transmission efficiency.

Section 10.4.3.5.3 Drive.

Section 10.4.3.5.3 – Add new Section 10.4.3.5.3 to read as follows:

10.4.3.5.3 Drive

Potential energy released during motion shall be recovered with a regenerative drive that supplies electrical energy to the building electrical system.

Section 10.4.4.1.1 Regenerative Drive.

Section 10.4.4.1.1 – Add new Section 10.4.4.1.1 to read as follows:

10.4.4.1.1 Regenerative Drive

An escalator designed either for one-way down operation only or for reversible operation shall have a variable frequency regenerative drive that supplies electrical energy to the building electrical system when the escalator is loaded with passengers whose combined weight exceeds 750 pounds.

Section 10.4.7.2	Recording and Reporting.

Section 10.4.7.2– Revise the exceptions to Section 10.4.7.2 to read as follows:

Exceptions to 10.4.7.1 and 10.4.7.2

1.	Buildings or additions less than 10,000 ft2.

2.	Individual tenant spaces less than 5,000 ft2.

3.	Dwelling units.

4.	Residential buildings with less than 10,000 ft2 of common area.

5.	Fuel used for on-site emergency equipment.

Section 10.4.11 Commercial Kitchen Equipment.

Section 10.4.11 – Add new Section 10.4.11 to read as follows:

10.4.11 Commercial Kitchen Equipment

Commercial kitchen equipment shall comply with the minimum efficiency requirements of Tables 10.4.11-1 through 10.4.11-5.

Table 10.4.11-1 Minimum Efficiency Requirements: Commercial Fryers

(This table is intended to be a restatement of the legally binding provisions found in Title 10 CFR Part 431 included here as a convenience to the users of this code)

|  | Heavy-Load Cooking Energy Efficiency | Idle Energy Rate | Test Procedure |
| --- | --- | --- | --- |
| Standard Open Deep-Fat Gas Fryers | ≥ 50% | ≤ 9,000 Btu/hr | ASTM Standard F1361-17 |
| Large Vat Open Deep-Fat Gas Fryers | ≥ 50% | ≤ 12,000 Btu/hr |  |
| Standard Open Deep-Fat Electric Fryers | ≥ 83% | ≤ 800 watts | ASTM Standard F2144-17 |
| Large Vat Open Deep-Fat Electric Fryers | ≥ 80% | ≤ 1,100 watts |  |

Table 10.4.11-2 Minimum Efficiency Requirements: Commercial Hot Food Holding Cabinets

(This table is intended to be a restatement of the legally binding provisions found in Title 10 CFR Part 431 included here as a convenience to the users of this code)

| Product Interior Volume (Cubic Feet) | Maximum Idle Energy Consumption Rate (Watts) | Test Procedure |
| --- | --- | --- |
| 0 < V < 13 | ≤ 21.5 V | ASTM Standard F2140-11 |
| 13 ≤ V < 28 | ≤ 2.0 V + 254.0 |  |
| 28 ≤ V | ≤ 3.8 V + 203.5 |  |

Table 10.4.11-3 Minimum Efficiency Requirements: Commercial Steam Cookers

(This table is intended to be a restatement of the legally binding provisions found in Title 10 CFR Part 431 included here as a convenience to the users of this code)

| Fuel Type | Pan Capacity | Cooking Energy Efficiencya | Idle Rate | Test Procedure |
| --- | --- | --- | --- | --- |
| Electric Steam | 3-pan | 50% | 400 watts | ASTM Standard F1484-18 |
|  | 4-pan 5-pan | 50% 50% | 530 watts 670 watts |  |
|  | 6-pan and larger | 50% | 800 watts |  |
| Gas Steam | 3-pan | 38% | 6,250 Btu/h |  |
|  | 4-pan | 38% | 8,350 Btu/h |  |
|  | 5-pan | 38% | 10,400 Btu/h |  |
|  | 6-pan and larger | 38% | 12,500 Btu/h |  |

Table 10.4.11-4 Minimum Efficiency Requirements: Commercial Dishwashers

(This table is intended to be a restatement of the legally binding provisions found in Title 10 CFR Part 431 included here as a convenience to the users of this code)

| High Temperature Efficiency Requirements Machine Type |  |  | Low Temperature Efficiency Requirements Test Procedure |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Idle Energy Ratea | Water Consumptionb | Idle Energy Ratea | Water Consumptionb |  |
| Under Counter | ≤ 0.50 kW | ≤ 0.86 GPR | ≤ 0.50 kW | ≤ 1.19 GPR |  |
| Stationary Single Tank Door | ≤ 0.70 kW | ≤ 0.89 GPR | ≤ 0.60 kW | ≤ 1.18 GPR | ASTM F1696-18 |
| Pot, Pan , and Utensil | ≤ 1.20 kW | ≤ 0.58 GPSF | ≤ 1.00 kW | ≤ 0.58 GPSF |  |
| Single Tank Conveyor | ≤ 1.50 kW | ≤ 0.70 GPR | ≤ 1.50 kW | ≤ 0.79 GPR | ASTM F1920-15 |
| Multiple Tank Conveyor | ≤ 2.25 kW | ≤ 0.54 GPR | ≤ 2.00 kW | ≤ 0.54 GPR |  |
| Single Tank Flight Type | Reported | GPH ≤ 2.975x + 55.00 | Reported | GPH ≤ 2.975x + 55.00 |  |
| Multiple Tank Flight Type | Reported | GPH ≤ 4.96x + 17.00 | Reported | GPH ≤ 4.96x + 17.00 |  |

a. Idle results shall be measured with the door closed and represent the total idle energy consumed by the machine including all tank heater(s) and controls. Booster heater (internal or external) energy consumption should not be part of this measurement unless it cannot be separately monitored per US EPA Energy Star Commercial Dishwasher Specification Version 2.0.

b. GPR = gallons per rack; GPSF = gallons per square foot of rack; GPH = gallons per hour; x = sf of conveyer belt (i.e., W*L/min (maximum conveyor speed).

Table 10.4.11-5 Minimum Efficiency Requirements: Commercial Ovens

(This table is intended to be a restatement of the legally binding provisions found in Title 10 CFR Part 431 included here as a convenience to the users of this code)

| Fuel Type | Classification | Idle Rate | Cooking-Energy Efficiency, % | Test Procedure |
| --- | --- | --- | --- | --- |
| Convection Ovens |  |  |  |  |
| Gas | Full-Size | ≤ 12,000 Btu/h | ≥ 46 | ASTM F1496 - 13 |
| Electric | Half-Size | ≤ 1.0 Btu/h | ≥ 71 |  |
|  | Full-Size | ≤ 1.60 Btu/h |  |  |
| Combination Ovens |  |  |  |  |
| Gas | Steam Mode | ≤ 200Pa + 6,511 Btu/h | ≥ 41 | ASTM F2861 - 17 |
|  | Convection Mode | ≤ 150Pa + 5,425 Btu/h | ≥ 56 |  |
| Electric | Steam Mode | ≤ 0.133Pa + 0.6400 kW | ≥ 55 |  |
|  | Convection Mode | ≤ 0.080Pa + 0.4989 kW | ≥ 76 |  |
| Rack Ovens |  |  |  |  |
| Gas | Single | ≤ 25,000 Btu/h | ≥ 48 | ASTM F2093 - 18 |
|  | Double | ≤ 30,000 Btu/h | ≥ 52 |  |

a. P = Pan Capacity: The number of steam table pans the combination oven is able to accommodate as per the ASTM F1495 – 05 standard specification.

Section 11- ADDITIONAL EFFICIENCY REQUIREMENTS.

Section 11.5.2 Energy Credits Achieved.

Section 11.5.2– Amend the first paragraph of  Section 11.5.2 to read as follows:

Energy credits achieved for the project shall be the sum of measure energy credits for individual measures included in the project. Energy credits shall only be counted to satisfy this code section if such systems, equipment or efficiencies exceed the requirements of any current state or local law, rule or regulation. Where a project contains multiple building use types, credits achieved for each building use type shall be weighted by the gross floor area of each building use type group to determine the weighted-average project energy credits achieved. The combined renewable (R01) and load management (G01 through G07) energy credits achieved through Section 11.5.2.6 and 11.5.2.8 shall be limited to meeting 60% of required energy credits. Credits are available for the measures listed in Section 11.5.2.1 through 11.5.2.8. Base energy credits are shown in Tables 11.5.3-1 through 11.5.3-9 for building use types in each climate zone. Measure energy credits achieved shall be determined in one of three ways, depending on the measure:

Section 11.5.2.3.1 Improved Service Water Heating Effectiveness.

Section 11.5.2.3.1 – Revise item “c” from Section 11.5.2.3.1 to read as follows:

c. Reserved

Section 11.5.2.3.1 – Revise item “d” from Section 11.5.2.3.1 to read as follows:

d. Combination service water heating systems shall achieve credits as follows:

1. (W01 + W02) Where service water heating employs both energy recovery and heat-pump water heating, W01 is permitted to be combined with W02 and receive the sum of both credits.

2. reserved

3. Reserved

4. Reserved

Section 11.5.2.7.1 Q01: Efficient Elevator Equipment.

Section 11.5.2.7.1 – Revise Section 11.5.2.7.1 to read as follows:

11.5.2.7.1 Q01: Efficient Elevator Equipment. Reserved.

Section 11.5.2.7.2 Q02: Efficient Kitchen Equipment.

Section 11.5.2.7.2 – Revise Section 11.5.2.7.2 to read as follows:

11.5.2.7.2 Q02: Efficient Kitchen Equipment. Reserved

Normative Appendix A- Rated R-Value of Insulation and Assembly U-Factor, C-Factor, and F-Factor Determinations.

Table A3.3.3. 1 Assembly U-factors for Steel-Frame Walls by Stud Spacing and Framing Factora,b

Table A3.3.3. 1 - Delete Table A3.3.3. 1 in its entirety and add new Table A3.3.3. 1 to read as follows:

Table A3.3.3. 1 Assembly U-factors for Steel-Frame Walls by Stud Spacing and Framing Factora,b

| Cavity Insulation Value | Base Wall U-factor at Framing | Overall U-Factor for Assembly of Base Wall Plus Continuous Insulation (Uninterrupted by Framing or Furring) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Rated R-Value of Continuous Insulation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 20 | 25 | 30 | 35 | 40 |
| Steel Framing at 12 in. on Center (25% Framing Factor)—includes framing for tracks, blocking, headers, and jamb and king studs |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 0.9 | 0.351 | 0.260 | 0.206 | 0.171 | 0.146 | 0.127 | 0.113 | 0.102 | 0.092 | 0.084 | 0.078 | 0.072 | 0.067 | 0.063 | 0.059 | 0.056 | 0.044 | 0.036 | 0.030 | 0.026 | 0.023 |  |
| 11 | 0.156 | 0.135 | 0.119 | 0.106 | 0.096 | 0.088 | 0.081 | 0.075 | 0.069 | 0.065 | 0.061 | 0.057 | 0.054 | 0.052 | 0.049 | 0.047 | 0.038 | 0.032 | 0.027 | 0.024 | 0.022 |  |
| 13 | 0.149 | 0.130 | 0.115 | 0.103 | 0.094 | 0.086 | 0.079 | 0.073 | 0.068 | 0.064 | 0.060 | 0.057 | 0.053 | 0.051 | 0.048 | 0.046 | 0.037 | 0.032 | 0.027 | 0.024 | 0.021 |  |
| 15 | 0.144 | 0.126 | 0.112 | 0.101 | 0.092 | 0.084 | 0.077 | 0.072 | 0.067 | 0.063 | 0.059 | 0.056 | 0.053 | 0.050 | 0.048 | 0.046 | 0.037 | 0.031 | 0.027 | 0.024 | 0.021 |  |
| 19 | 0.137 | 0.121 | 0.108 | 0.097 | 0.089 | 0.081 | 0.075 | 0.070 | 0.065 | 0.061 | 0.058 | 0.055 | 0.052 | 0.049 | 0.047 | 0.045 | 0.037 | 0.031 | 0.027 | 0.024 | 0.021 |  |
| 21 | 0.135 | 0.119 | 0.106 | 0.096 | 0.088 | 0.080 | 0.074 | 0.069 | 0.065 | 0.061 | 0.057 | 0.054 | 0.051 | 0.049 | 0.047 | 0.045 | 0.036 | 0.031 | 0.027 | 0.024 | 0.021 |  |
| 25 | 0.131 | 0.116 | 0.104 | 0.094 | 0.086 | 0.079 | 0.073 | 0.068 | 0.064 | 0.060 | 0.057 | 0.054 | 0.051 | 0.048 | 0.046 | 0.044 | 0.036 | 0.031 | 0.027 | 0.023 | 0.021 |  |
| 30 | 0.127 | 0.113 | 0.101 | 0.092 | 0.084 | 0.078 | 0.072 | 0.067 | 0.063 | 0.059 | 0.056 | 0.053 | 0.050 | 0.048 | 0.046 | 0.044 | 0.036 | 0.030 | 0.026 | 0.023 | 0.021 |  |
| Steel Framing at 16 in. on Center (22% Framing Factor)—includes framing for tracks, blocking, headers, and jamb and king studs |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 0.9 | 0.350 | 0.259 | 0.206 | 0.171 | 0.146 | 0.127 | 0.113 | 0.101 | 0.092 | 0.084 | 0.078 | 0.072 | 0.067 | 0.063 | 0.059 | 0.056 | 0.044 | 0.036 | 0.030 | 0.026 | 0.023 |  |
| 11 | 0.148 | 0.129 | 0.114 | 0.103 | 0.093 | 0.085 | 0.078 | 0.073 | 0.068 | 0.063 | 0.060 | 0.056 | 0.053 | 0.051 | 0.048 | 0.046 | 0.037 | 0.031 | 0.027 | 0.024 | 0.021 |  |
| 13 | 0.141 | 0.124 | 0.110 | 0.099 | 0.090 | 0.083 | 0.076 | 0.071 | 0.066 | 0.062 | 0.059 | 0.055 | 0.052 | 0.050 | 0.047 | 0.045 | 0.037 | 0.031 | 0.027 | 0.024 | 0.021 |  |
| 15 | 0.136 | 0.120 | 0.107 | 0.097 | 0.088 | 0.081 | 0.075 | 0.070 | 0.065 | 0.061 | 0.058 | 0.054 | 0.052 | 0.049 | 0.047 | 0.045 | 0.037 | 0.031 | 0.027 | 0.024 | 0.021 |  |
| 19 | 0.129 | 0.114 | 0.102 | 0.093 | 0.085 | 0.078 | 0.073 | 0.068 | 0.063 | 0.060 | 0.056 | 0.053 | 0.051 | 0.048 | 0.046 | 0.044 | 0.036 | 0.031 | 0.026 | 0.023 | 0.021 |  |
| 21 | 0.126 | 0.112 | 0.100 | 0.091 | 0.084 | 0.077 | 0.072 | 0.067 | 0.063 | 0.059 | 0.056 | 0.053 | 0.050 | 0.048 | 0.046 | 0.044 | 0.036 | 0.030 | 0.026 | 0.023 | 0.021 |  |
| 25 | 0.122 | 0.108 | 0.098 | 0.089 | 0.082 | 0.076 | 0.070 | 0.066 | 0.062 | 0.058 | 0.055 | 0.052 | 0.049 | 0.047 | 0.045 | 0.043 | 0.035 | 0.030 | 0.026 | 0.023 | 0.021 |  |
| 30 | 0.118 | 0.105 | 0.095 | 0.087 | 0.080 | 0.074 | 0.069 | 0.065 | 0.061 | 0.057 | 0.054 | 0.051 | 0.049 | 0.047 | 0.044 | 0.043 | 0.035 | 0.030 | 0.026 | 0.023 | 0.021 |  |
| Steel Framing at 24 in. on Center (18% Framing Factor)—includes framing for tracks, blocking, headers, and jamb and king studs |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 0.9 | 0.348 | 0.258 | 0.205 | 0.170 | 0.145 | 0.127 | 0.113 | 0.101 | 0.092 | 0.084 | 0.078 | 0.072 | 0.067 | 0.063 | 0.059 | 0.056 | 0.044 | 0.036 | 0.030 | 0.026 | 0.023 |  |
| 11 | 0.137 | 0.121 | 0.108 | 0.097 | 0.089 | 0.081 | 0.075 | 0.070 | 0.065 | 0.061 | 0.058 | 0.055 | 0.052 | 0.049 | 0.047 | 0.045 | 0.037 | 0.031 | 0.027 | 0.024 | 0.021 |  |
| 13 | 0.130 | 0.115 | 0.103 | 0.093 | 0.085 | 0.079 | 0.073 | 0.068 | 0.064 | 0.060 | 0.056 | 0.053 | 0.051 | 0.048 | 0.046 | 0.044 | 0.036 | 0.031 | 0.027 | 0.023 | 0.021 |  |
| 15 | 0.124 | 0.110 | 0.099 | 0.090 | 0.083 | 0.077 | 0.071 | 0.066 | 0.062 | 0.059 | 0.055 | 0.052 | 0.050 | 0.047 | 0.045 | 0.043 | 0.036 | 0.030 | 0.026 | 0.023 | 0.021 |  |
| 19 | 0.116 | 0.104 | 0.094 | 0.086 | 0.079 | 0.073 | 0.068 | 0.064 | 0.060 | 0.057 | 0.054 | 0.051 | 0.049 | 0.046 | 0.044 | 0.042 | 0.035 | 0.030 | 0.026 | 0.023 | 0.021 |  |
| 21 | 0.113 | 0.102 | 0.092 | 0.084 | 0.078 | 0.072 | 0.067 | 0.063 | 0.059 | 0.056 | 0.053 | 0.050 | 0.048 | 0.046 | 0.044 | 0.042 | 0.035 | 0.030 | 0.026 | 0.023 | 0.020 |  |
| 25 | 0.109 | 0.098 | 0.089 | 0.082 | 0.076 | 0.070 | 0.066 | 0.062 | 0.058 | 0.055 | 0.052 | 0.049 | 0.047 | 0.045 | 0.043 | 0.041 | 0.034 | 0.029 | 0.026 | 0.023 | 0.020 |  |
| 30 | 0.105 | 0.095 | 0.086 | 0.080 | 0.074 | 0.069 | 0.064 | 0.060 | 0.057 | 0.054 | 0.051 | 0.049 | 0.046 | 0.044 | 0.042 | 0.041 | 0.034 | 0.029 | 0.025 | 0.022 | 0.020 |  |
| Steel Framing at 12 in. on Center (18% Framing Factor)—includes only studs at 12 in. on center and top and bottom tracks |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 0.9 | 0.348 | 0.258 | 0.205 | 0.170 | 0.145 | 0.127 | 0.113 | 0.101 | 0.092 | 0.084 | 0.078 | 0.072 | 0.067 | 0.063 | 0.059 | 0.056 | 0.044 | 0.036 | 0.030 | 0.026 | 0.023 |  |
| 11 | 0.137 | 0.121 | 0.108 | 0.097 | 0.089 | 0.081 | 0.075 | 0.070 | 0.065 | 0.061 | 0.058 | 0.055 | 0.052 | 0.049 | 0.047 | 0.045 | 0.037 | 0.031 | 0.027 | 0.024 | 0.021 |  |
| 13 | 0.130 | 0.115 | 0.103 | 0.093 | 0.085 | 0.079 | 0.073 | 0.068 | 0.064 | 0.060 | 0.056 | 0.053 | 0.051 | 0.048 | 0.046 | 0.044 | 0.036 | 0.031 | 0.027 | 0.023 | 0.021 |  |
| 15 | 0.124 | 0.110 | 0.099 | 0.090 | 0.083 | 0.077 | 0.071 | 0.066 | 0.062 | 0.059 | 0.055 | 0.052 | 0.050 | 0.047 | 0.045 | 0.043 | 0.036 | 0.030 | 0.026 | 0.023 | 0.021 |  |
| 19 | 0.116 | 0.104 | 0.094 | 0.086 | 0.079 | 0.073 | 0.068 | 0.064 | 0.060 | 0.057 | 0.054 | 0.051 | 0.049 | 0.046 | 0.044 | 0.042 | 0.035 | 0.030 | 0.026 | 0.023 | 0.021 |  |
| 21 | 0.113 | 0.102 | 0.092 | 0.084 | 0.078 | 0.072 | 0.067 | 0.063 | 0.059 | 0.056 | 0.053 | 0.050 | 0.048 | 0.046 | 0.044 | 0.042 | 0.035 | 0.030 | 0.026 | 0.023 | 0.020 |  |
| 25 | 0.109 | 0.098 | 0.089 | 0.082 | 0.076 | 0.070 | 0.066 | 0.062 | 0.058 | 0.055 | 0.052 | 0.049 | 0.047 | 0.045 | 0.043 | 0.041 | 0.034 | 0.029 | 0.026 | 0.023 | 0.020 |  |
| 30 | 0.105 | 0.095 | 0.086 | 0.080 | 0.074 | 0.069 | 0.064 | 0.060 | 0.057 | 0.054 | 0.051 | 0.049 | 0.046 | 0.044 | 0.042 | 0.041 | 0.034 | 0.029 | 0.025 | 0.022 | 0.020 |  |
| Steel Framing at 16 in. on Center (14% Framing Factor)—includes only studs at 16 in. on center and top and bottom tracks |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 0.9 | 0.346 | 0.257 | 0.204 | 0.170 | 0.145 | 0.127 | 0.112 | 0.101 | 0.092 | 0.084 | 0.078 | 0.072 | 0.067 | 0.063 | 0.059 | 0.056 | 0.044 | 0.036 | 0.030 | 0.026 | 0.023 |  |
| 11 | 0.125 | 0.111 | 0.100 | 0.091 | 0.083 | 0.077 | 0.071 | 0.067 | 0.063 | 0.059 | 0.056 | 0.053 | 0.050 | 0.048 | 0.045 | 0.044 | 0.036 | 0.030 | 0.026 | 0.023 | 0.021 |  |
| 13 | 0.117 | 0.105 | 0.095 | 0.087 | 0.080 | 0.074 | 0.069 | 0.064 | 0.061 | 0.057 | 0.054 | 0.051 | 0.049 | 0.046 | 0.044 | 0.043 | 0.035 | 0.030 | 0.026 | 0.023 | 0.021 |  |
| 15 | 0.111 | 0.100 | 0.091 | 0.083 | 0.077 | 0.072 | 0.067 | 0.063 | 0.059 | 0.056 | 0.053 | 0.050 | 0.048 | 0.045 | 0.044 | 0.042 | 0.035 | 0.029 | 0.026 | 0.023 | 0.020 |  |
| 19 | 0.103 | 0.093 | 0.085 | 0.079 | 0.073 | 0.068 | 0.064 | 0.060 | 0.056 | 0.053 | 0.051 | 0.048 | 0.046 | 0.044 | 0.042 | 0.040 | 0.034 | 0.029 | 0.025 | 0.022 | 0.020 |  |
| 21 | 0.100 | 0.091 | 0.083 | 0.077 | 0.071 | 0.066 | 0.062 | 0.059 | 0.055 | 0.053 | 0.050 | 0.048 | 0.045 | 0.043 | 0.042 | 0.040 | 0.033 | 0.029 | 0.025 | 0.022 | 0.020 |  |
| 25 | 0.095 | 0.087 | 0.080 | 0.074 | 0.069 | 0.064 | 0.060 | 0.057 | 0.054 | 0.051 | 0.049 | 0.046 | 0.044 | 0.042 | 0.041 | 0.039 | 0.033 | 0.028 | 0.025 | 0.022 | 0.020 |  |
| 30 | 0.090 | 0.083 | 0.077 | 0.071 | 0.066 | 0.062 | 0.059 | 0.055 | 0.052 | 0.050 | 0.047 | 0.045 | 0.043 | 0.042 | 0.040 | 0.038 | 0.032 | 0.028 | 0.024 | 0.022 | 0.020 |  |
| Steel Framing at 24 in. on Center (10% Framing Factor)—includes only studs at 24 in. on center and top and bottom tracks |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 0.9 | 0.344 | 0.256 | 0.204 | 0.169 | 0.145 | 0.126 | 0.112 | 0.101 | 0.092 | 0.084 | 0.077 | 0.072 | 0.067 | 0.063 | 0.059 | 0.056 | 0.044 | 0.036 | 0.030 | 0.026 | 0.023 |  |
| 11 | 0.113 | 0.101 | 0.092 | 0.084 | 0.078 | 0.072 | 0.067 | 0.063 | 0.059 | 0.056 | 0.053 | 0.050 | 0.048 | 0.046 | 0.044 | 0.042 | 0.035 | 0.030 | 0.026 | 0.023 | 0.020 |  |
| 13 | 0.104 | 0.094 | 0.086 | 0.079 | 0.073 | 0.068 | 0.064 | 0.060 | 0.057 | 0.054 | 0.051 | 0.049 | 0.046 | 0.044 | 0.042 | 0.041 | 0.034 | 0.029 | 0.025 | 0.022 | 0.020 |  |
| 15 | 0.098 | 0.089 | 0.082 | 0.076 | 0.070 | 0.066 | 0.062 | 0.058 | 0.055 | 0.052 | 0.049 | 0.047 | 0.045 | 0.043 | 0.041 | 0.040 | 0.033 | 0.028 | 0.025 | 0.022 | 0.020 |  |
| 19 | 0.088 | 0.081 | 0.075 | 0.070 | 0.065 | 0.061 | 0.058 | 0.055 | 0.052 | 0.049 | 0.047 | 0.045 | 0.043 | 0.041 | 0.040 | 0.038 | 0.032 | 0.028 | 0.024 | 0.022 | 0.019 |  |
| 21 | 0.085 | 0.078 | 0.073 | 0.068 | 0.063 | 0.060 | 0.056 | 0.053 | 0.051 | 0.048 | 0.046 | 0.044 | 0.042 | 0.040 | 0.039 | 0.037 | 0.031 | 0.027 | 0.024 | 0.021 | 0.019 |  |
| 25 | 0.080 | 0.074 | 0.069 | 0.064 | 0.060 | 0.057 | 0.054 | 0.051 | 0.049 | 0.046 | 0.044 | 0.042 | 0.041 | 0.039 | 0.038 | 0.036 | 0.031 | 0.027 | 0.024 | 0.021 | 0.019 |  |
| 30 | 0.075 | 0.070 | 0.065 | 0.061 | 0.058 | 0.055 | 0.052 | 0.049 | 0.047 | 0.045 | 0.043 | 0.041 | 0.039 | 0.038 | 0.037 | 0.035 | 0.030 | 0.026 | 0.023 | 0.021 | 0.019 |  |

|  |  | Overall U-Factor for Assembly of Base Wall Plus Continuous Insulation (Uninterrupted by Framing or Furring) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Cavity Insulation Value | Base Wall U-factor at Framing | Rated R-Value of Continuous Insulation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 0.18 | 0.35 | 0.53 | 0.70 | 0.88 | 1.06 | 1.23 | 1.41 | 1.59 | 1.76 | 1.94 | 2.11 | 2.29 | 2.47 | 2.64 | 3.52 | 4.40 | 5.28 | 6.16 | 7.04 |
| Steel Framing at 300 mm on Center (25% Framing Factor)—includes framing for tracks, blocking, headers, and jamb and king studs |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 0.16 | 1.99 | 1.47 | 1.17 | 0.97 | 0.83 | 0.72 | 0.64 | 0.58 | 0.52 | 0.48 | 0.44 | 0.41 | 0.38 | 0.36 | 0.34 | 0.32 | 0.25 | 0.20 | 0.17 | 0.15 | 0.13 |  |
| 1.94 | 0.89 | 0.77 | 0.68 | 0.60 | 0.55 | 0.50 | 0.46 | 0.42 | 0.39 | 0.37 | 0.35 | 0.33 | 0.31 | 0.29 | 0.28 | 0.27 | 0.21 | 0.18 | 0.16 | 0.14 | 0.12 |  |
| 2.29 | 0.85 | 0.74 | 0.65 | 0.59 | 0.53 | 0.49 | 0.45 | 0.41 | 0.39 | 0.36 | 0.34 | 0.32 | 0.30 | 0.29 | 0.27 | 0.26 | 0.21 | 0.18 | 0.15 | 0.14 | 0.12 |  |
| 2.64 | 0.82 | 0.72 | 0.64 | 0.57 | 0.52 | 0.48 | 0.44 | 0.41 | 0.38 | 0.36 | 0.34 | 0.32 | 0.30 | 0.28 | 0.27 | 0.26 | 0.21 | 0.18 | 0.15 | 0.14 | 0.12 |  |
| 3.35 | 0.78 | 0.69 | 0.61 | 0.55 | 0.50 | 0.46 | 0.43 | 0.40 | 0.37 | 0.35 | 0.33 | 0.31 | 0.29 | 0.28 | 0.27 | 0.25 | 0.21 | 0.18 | 0.15 | 0.13 | 0.12 |  |
| 3.70 | 0.76 | 0.67 | 0.60 | 0.54 | 0.50 | 0.46 | 0.42 | 0.39 | 0.37 | 0.35 | 0.33 | 0.31 | 0.29 | 0.28 | 0.27 | 0.25 | 0.21 | 0.18 | 0.15 | 0.13 | 0.12 |  |
| 4.40 | 0.74 | 0.66 | 0.59 | 0.53 | 0.49 | 0.45 | 0.42 | 0.39 | 0.36 | 0.34 | 0.32 | 0.30 | 0.29 | 0.27 | 0.26 | 0.25 | 0.21 | 0.17 | 0.15 | 0.13 | 0.12 |  |
| 5.28 | 0.72 | 0.64 | 0.58 | 0.52 | 0.48 | 0.44 | 0.41 | 0.38 | 0.36 | 0.34 | 0.32 | 0.30 | 0.29 | 0.27 | 0.26 | 0.25 | 0.20 | 0.17 | 0.15 | 0.13 | 0.12 |  |
| Steel Framing at 400 mm on Center (22% Framing Factor)—includes framing for tracks, blocking, headers, and jamb and king studs |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 0.16 | 1.98 | 1.47 | 1.17 | 0.97 | 0.83 | 0.72 | 0.64 | 0.58 | 0.52 | 0.48 | 0.44 | 0.41 | 0.38 | 0.36 | 0.34 | 0.32 | 0.25 | 0.20 | 0.17 | 0.15 | 0.13 |  |
| 1.94 | 0.84 | 0.73 | 0.65 | 0.58 | 0.53 | 0.48 | 0.45 | 0.41 | 0.38 | 0.36 | 0.34 | 0.32 | 0.30 | 0.29 | 0.27 | 0.26 | 0.21 | 0.18 | 0.15 | 0.14 | 0.12 |  |
| 2.29 | 0.80 | 0.70 | 0.63 | 0.56 | 0.51 | 0.47 | 0.43 | 0.40 | 0.38 | 0.35 | 0.33 | 0.31 | 0.30 | 0.28 | 0.27 | 0.26 | 0.21 | 0.18 | 0.15 | 0.13 | 0.12 |  |
| 2.64 | 0.77 | 0.68 | 0.61 | 0.55 | 0.50 | 0.46 | 0.43 | 0.40 | 0.37 | 0.35 | 0.33 | 0.31 | 0.29 | 0.28 | 0.27 | 0.25 | 0.21 | 0.18 | 0.15 | 0.13 | 0.12 |  |
| 3.35 | 0.73 | 0.65 | 0.58 | 0.53 | 0.48 | 0.44 | 0.41 | 0.38 | 0.36 | 0.34 | 0.32 | 0.30 | 0.29 | 0.27 | 0.26 | 0.25 | 0.20 | 0.17 | 0.15 | 0.13 | 0.12 |  |
| 3.70 | 0.71 | 0.63 | 0.57 | 0.52 | 0.48 | 0.44 | 0.41 | 0.38 | 0.36 | 0.33 | 0.32 | 0.30 | 0.28 | 0.27 | 0.26 | 0.25 | 0.20 | 0.17 | 0.15 | 0.13 | 0.12 |  |
| 4.40 | 0.69 | 0.62 | 0.56 | 0.51 | 0.46 | 0.43 | 0.40 | 0.37 | 0.35 | 0.33 | 0.31 | 0.30 | 0.28 | 0.27 | 0.26 | 0.24 | 0.20 | 0.17 | 0.15 | 0.13 | 0.12 |  |
| 5.28 | 0.67 | 0.60 | 0.54 | 0.49 | 0.45 | 0.42 | 0.39 | 0.37 | 0.34 | 0.32 | 0.31 | 0.29 | 0.28 | 0.26 | 0.25 | 0.24 | 0.20 | 0.17 | 0.15 | 0.13 | 0.12 |  |
| Steel Framing at 600 mm on Center (18% Framing Factor)—includes framing for tracks, blocking, headers, and jamb and king studs |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 0.16 | 1.97 | 1.46 | 1.16 | 0.97 | 0.83 | 0.72 | 0.64 | 0.57 | 0.52 | 0.48 | 0.44 | 0.41 | 0.38 | 0.36 | 0.34 | 0.32 | 0.25 | 0.20 | 0.17 | 0.15 | 0.13 |  |
| 1.94 | 0.78 | 0.68 | 0.61 | 0.55 | 0.50 | 0.46 | 0.43 | 0.40 | 0.37 | 0.35 | 0.33 | 0.31 | 0.29 | 0.28 | 0.27 | 0.25 | 0.21 | 0.18 | 0.15 | 0.13 | 0.12 |  |
| 2.29 | 0.74 | 0.65 | 0.58 | 0.53 | 0.48 | 0.45 | 0.41 | 0.39 | 0.36 | 0.34 | 0.32 | 0.30 | 0.29 | 0.27 | 0.26 | 0.25 | 0.20 | 0.17 | 0.15 | 0.13 | 0.12 |  |
| 2.64 | 0.70 | 0.63 | 0.56 | 0.51 | 0.47 | 0.43 | 0.40 | 0.38 | 0.35 | 0.33 | 0.31 | 0.30 | 0.28 | 0.27 | 0.26 | 0.25 | 0.20 | 0.17 | 0.15 | 0.13 | 0.12 |  |
| 3.35 | 0.66 | 0.59 | 0.53 | 0.49 | 0.45 | 0.42 | 0.39 | 0.36 | 0.34 | 0.32 | 0.31 | 0.29 | 0.28 | 0.26 | 0.25 | 0.24 | 0.20 | 0.17 | 0.15 | 0.13 | 0.12 |  |
| 3.70 | 0.64 | 0.58 | 0.52 | 0.48 | 0.44 | 0.41 | 0.38 | 0.36 | 0.34 | 0.32 | 0.30 | 0.29 | 0.27 | 0.26 | 0.25 | 0.24 | 0.20 | 0.17 | 0.15 | 0.13 | 0.12 |  |
| 4.40 | 0.62 | 0.56 | 0.51 | 0.47 | 0.43 | 0.40 | 0.37 | 0.35 | 0.33 | 0.31 | 0.30 | 0.28 | 0.27 | 0.26 | 0.24 | 0.23 | 0.19 | 0.17 | 0.14 | 0.13 | 0.12 |  |
| 5.28 | 0.59 | 0.54 | 0.49 | 0.45 | 0.42 | 0.39 | 0.36 | 0.34 | 0.32 | 0.31 | 0.29 | 0.28 | 0.26 | 0.25 | 0.24 | 0.23 | 0.19 | 0.16 | 0.14 | 0.13 | 0.11 |  |

| Cavity Insulation Value | Base Wall U-factor at Framing | Overall U-Factor for Assembly of Base Wall Plus Continuous Insulation (Uninterrupted by Framing or Furring) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Rated R-Value of Continuous Insulation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | 0.18 | 0.35 | 0.53 | 0.70 | 0.88 | 1.06 | 1.23 | 1.41 | 1.59 | 1.76 | 1.94 | 2.11 | 2.29 | 2.47 | 2.64 | 3.52 | 4.40 | 5.28 | 6.16 | 7.04 |
| Steel Framing at 300 mm on Center (18% Framing Factor)—includes only studs at 300 mm on center and top and bottom tracks |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 0.16 | 1.97 | 1.46 | 1.16 | 0.97 | 0.83 | 0.72 | 0.64 | 0.57 | 0.52 | 0.48 | 0.44 | 0.41 | 0.38 | 0.36 | 0.34 | 0.32 | 0.25 | 0.20 | 0.17 | 0.15 | 0.13 |  |
| 1.94 | 0.78 | 0.68 | 0.61 | 0.55 | 0.50 | 0.46 | 0.43 | 0.40 | 0.37 | 0.35 | 0.33 | 0.31 | 0.29 | 0.28 | 0.27 | 0.25 | 0.21 | 0.18 | 0.15 | 0.13 | 0.12 |  |
| 2.29 | 0.74 | 0.65 | 0.58 | 0.53 | 0.48 | 0.45 | 0.41 | 0.39 | 0.36 | 0.34 | 0.32 | 0.30 | 0.29 | 0.27 | 0.26 | 0.25 | 0.20 | 0.17 | 0.15 | 0.13 | 0.12 |  |
| 2.64 | 0.70 | 0.63 | 0.56 | 0.51 | 0.47 | 0.43 | 0.40 | 0.38 | 0.35 | 0.33 | 0.31 | 0.30 | 0.28 | 0.27 | 0.26 | 0.25 | 0.20 | 0.17 | 0.15 | 0.13 | 0.12 |  |
| 3.35 | 0.66 | 0.59 | 0.53 | 0.49 | 0.45 | 0.42 | 0.39 | 0.36 | 0.34 | 0.32 | 0.31 | 0.29 | 0.28 | 0.26 | 0.25 | 0.24 | 0.20 | 0.17 | 0.15 | 0.13 | 0.12 |  |
| 3.70 | 0.64 | 0.58 | 0.52 | 0.48 | 0.44 | 0.41 | 0.38 | 0.36 | 0.34 | 0.32 | 0.30 | 0.29 | 0.27 | 0.26 | 0.25 | 0.24 | 0.20 | 0.17 | 0.15 | 0.13 | 0.12 |  |
| 4.40 | 0.62 | 0.56 | 0.51 | 0.47 | 0.43 | 0.40 | 0.37 | 0.35 | 0.33 | 0.31 | 0.30 | 0.28 | 0.27 | 0.26 | 0.24 | 0.23 | 0.19 | 0.17 | 0.14 | 0.13 | 0.12 |  |
| 5.28 | 0.59 | 0.54 | 0.49 | 0.45 | 0.42 | 0.39 | 0.36 | 0.34 | 0.32 | 0.31 | 0.29 | 0.28 | 0.26 | 0.25 | 0.24 | 0.23 | 0.19 | 0.16 | 0.14 | 0.13 | 0.11 |  |
| Steel Framing at 400 mm on Center (14% Framing Factor)—includes only studs at 400 mm on center and top and bottom tracks |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 0.16 | 1.96 | 1.46 | 1.16 | 0.96 | 0.82 | 0.72 | 0.64 | 0.57 | 0.52 | 0.48 | 0.44 | 0.41 | 0.38 | 0.36 | 0.34 | 0.32 | 0.25 | 0.20 | 0.17 | 0.15 | 0.13 |  |
| 1.94 | 0.71 | 0.63 | 0.57 | 0.52 | 0.47 | 0.44 | 0.41 | 0.38 | 0.36 | 0.33 | 0.32 | 0.30 | 0.28 | 0.27 | 0.26 | 0.25 | 0.20 | 0.17 | 0.15 | 0.13 | 0.12 |  |
| 2.29 | 0.67 | 0.60 | 0.54 | 0.49 | 0.45 | 0.42 | 0.39 | 0.37 | 0.34 | 0.32 | 0.31 | 0.29 | 0.28 | 0.26 | 0.25 | 0.24 | 0.20 | 0.17 | 0.15 | 0.13 | 0.12 |  |
| 2.64 | 0.63 | 0.57 | 0.52 | 0.47 | 0.44 | 0.41 | 0.38 | 0.36 | 0.33 | 0.32 | 0.30 | 0.28 | 0.27 | 0.26 | 0.25 | 0.24 | 0.20 | 0.17 | 0.15 | 0.13 | 0.12 |  |
| 3.35 | 0.58 | 0.53 | 0.48 | 0.45 | 0.41 | 0.39 | 0.36 | 0.34 | 0.32 | 0.30 | 0.29 | 0.27 | 0.26 | 0.25 | 0.24 | 0.23 | 0.19 | 0.16 | 0.14 | 0.13 | 0.11 |  |
| 3.70 | 0.57 | 0.51 | 0.47 | 0.44 | 0.40 | 0.38 | 0.35 | 0.33 | 0.31 | 0.30 | 0.28 | 0.27 | 0.26 | 0.25 | 0.24 | 0.23 | 0.19 | 0.16 | 0.14 | 0.13 | 0.11 |  |
| 4.40 | 0.54 | 0.49 | 0.45 | 0.42 | 0.39 | 0.36 | 0.34 | 0.32 | 0.31 | 0.29 | 0.28 | 0.26 | 0.25 | 0.24 | 0.23 | 0.22 | 0.19 | 0.16 | 0.14 | 0.12 | 0.11 |  |
| 5.28 | 0.51 | 0.47 | 0.43 | 0.40 | 0.38 | 0.35 | 0.33 | 0.31 | 0.30 | 0.28 | 0.27 | 0.26 | 0.25 | 0.24 | 0.23 | 0.22 | 0.18 | 0.16 | 0.14 | 0.12 | 0.11 |  |
| Steel Framing at 600 mm on Center (10% Framing Factor)—includes only studs at 600 mm on center and top and bottom tracks |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 0.16 | 1.95 | 1.45 | 1.16 | 0.96 | 0.82 | 0.72 | 0.64 | 0.57 | 0.52 | 0.48 | 0.44 | 0.41 | 0.38 | 0.36 | 0.34 | 0.32 | 0.25 | 0.20 | 0.17 | 0.15 | 0.13 |  |
| 1.94 | 0.64 | 0.57 | 0.52 | 0.48 | 0.44 | 0.41 | 0.38 | 0.36 | 0.34 | 0.32 | 0.30 | 0.29 | 0.27 | 0.26 | 0.25 | 0.24 | 0.20 | 0.17 | 0.15 | 0.13 | 0.12 |  |
| 2.29 | 0.59 | 0.54 | 0.49 | 0.45 | 0.42 | 0.39 | 0.36 | 0.34 | 0.32 | 0.31 | 0.29 | 0.28 | 0.26 | 0.25 | 0.24 | 0.23 | 0.19 | 0.16 | 0.14 | 0.13 | 0.11 |  |
| 2.64 | 0.55 | 0.51 | 0.46 | 0.43 | 0.40 | 0.37 | 0.35 | 0.33 | 0.31 | 0.30 | 0.28 | 0.27 | 0.26 | 0.24 | 0.23 | 0.22 | 0.19 | 0.16 | 0.14 | 0.13 | 0.11 |  |
| 3.35 | 0.50 | 0.46 | 0.43 | 0.40 | 0.37 | 0.35 | 0.33 | 0.31 | 0.29 | 0.28 | 0.27 | 0.25 | 0.24 | 0.23 | 0.22 | 0.22 | 0.18 | 0.16 | 0.14 | 0.12 | 0.11 |  |
| 3.70 | 0.48 | 0.45 | 0.41 | 0.38 | 0.36 | 0.34 | 0.32 | 0.30 | 0.29 | 0.27 | 0.26 | 0.25 | 0.24 | 0.23 | 0.22 | 0.21 | 0.18 | 0.15 | 0.14 | 0.12 | 0.11 |  |
| 4.40 | 0.45 | 0.42 | 0.39 | 0.37 | 0.34 | 0.32 | 0.31 | 0.29 | 0.28 | 0.26 | 0.25 | 0.24 | 0.23 | 0.22 | 0.21 | 0.21 | 0.17 | 0.15 | 0.13 | 0.12 | 0.11 |  |
| 5.28 | 0.43 | 0.40 | 0.37 | 0.35 | 0.33 | 0.31 | 0.29 | 0.28 | 0.27 | 0.25 | 0.24 | 0.23 | 0.22 | 0.22 | 0.21 | 0.20 | 0.17 | 0.15 | 0.13 | 0.12 | 0.11 |  |

a. Refer to Section A9.2(b)(3)(i) for calculation method used to generate table values.

b. The cavity insulation rated RSI-value of 0.16 corresponds to no cavity insulation.

Section A10.2.1 Thermal bridge details.

Section A10.2.1- Add new section A10.2.1 to read as follows:

A10.2.1 Thermal bridge details.

Psi-factors and chi-factors for thermal bridges shall be determined in accordance with Normative Appendix A, Section A10. The following intersections shall be evaluated for thermal bridges and be detailed in construction documents:

- Structural framing and members.

- Cladding attachment systems

- Assembly intersections:

- Roof edge, parapet

- Intermediate floor to wall intersection

- Intermediate floor balcony or overhang to opaque wall intersection

- Intermediate floor balcony in contact with vertical fenestration

- Cladding support

- Wall to vertical fenestration intersection

Details shall include the total length of each linear thermal bridge, corresponding psi-factors and source. Details shall include point thermal bridges, including their cross-sectional area and quantity of each type, corresponding chi-factors and source.

Exception: HVAC or electrical system point thermal bridges totaling less than 12 square inches (7742 mm2) of cross-sectional area at exposure.

Normative Appendix C- Methodology for Building Envelope Trade-Off Option in Section 5.6.

Section C3.5.5.4 Thermal Bridges.

Section C3.5.5.4 – Revise  Section C3.5.5.4 to read as follows:

C3.5.5.4 Thermal Bridges.

Linear and point thermal bridges in the proposed design shall be one of the following:

a. Not modeled where option (a) or (c) is selected in Section C1.2.7.

b. Entered as individual thermal bridge inputs of length or count where option (b) is selected in Section C1.2.7 and addressed as follows:

1. Individual thermal bridges in the proposed design that are indicated to comply with the requirements of Sections 5.5.5.1 through 5.5.5.5 shall be modeled with the user-defined psi-factor or chi-factors or the default values from Table A10.1.

2. Individual thermal bridges in the proposed design that are indicated to not comply with the requirements of Sections 5.5.5.1 through 5.5.5.5 shall be modeled with the user-defined psi-factor or chi-factors or the unmitigated values from Table A10.1.

3. Individual thermal bridges in the proposed design that are indicated to be not applicable with the requirements of Sections 5.5.5.1 through 5.5.5.5 need not be modeled.

Normative Appendix G- Performance Rating Method.

Section G1.4 Energy Modeler Qualifications.

Section G1.4 – Add new Section G1.4 to read as follows:

G1.4 Energy Modeler Qualifications

Energy models shall be created by persons qualified by education and training to perform such work. The submitted modeling documentation shall include the name, affiliation, credentials, and contact information of either a registered design professional be signed either with a minimum of two years of experience in modeling buildings of similar size and complexity or an individual with an active certification from ASHRAE as a Building Energy Modeling Professional (BEMP) that completed or supervised the energy modeling.

§ 4. This local law shall take effect on the same date of that New York State Energy Conservation Construction Code, as adopted on October 1, 2025, by the State Fire Prevention and Building Code Council pursuant to Article 11 of the New York State Energy Law, takes effect, except that if this local law becomes law after such date, it is retroactive to and deemed to have been in effect as of the effective date of such  New York State Energy Conservation Construction Code.